## Hoja1
PROPERTIES
General
Name | Gamesa G128 4.5MW Class IIA
Manufacturer | Gamesa
Hub Height | 5+ | 95 | 120 | 140
Power
Rated Power | 4500
Peak Power | 4500
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 128
Number of blades | 3
Rated RPM | 11.84
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 30
Restart Wind Speed | 30
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -20
High Temperature Shutdown | 40
High Temperature Restart | 40
Comments and details

## Hoja2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | II
Turbine SubClass | A
Values
Certification | IEC 3rd Edition Amendment
Vave | 8.5
Vref | 42.5
Design TI | 0.16

## Hoja3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.03 | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.24 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 42 | 45 | 48 | 50 | 53 | 55 | 58 | 59 | 60 | 63
| 4 | 156 | 162 | 168 | 174 | 180 | 186 | 192 | 195 | 198 | 204
| 5 | 344 | 356 | 368 | 379 | 391 | 403 | 414 | 420 | 426 | 438
| 6 | 628 | 648 | 668 | 688 | 709 | 729 | 749 | 759 | 769 | 789
| 7 | 1025 | 1057 | 1089 | 1121 | 1152 | 1184 | 1215 | 1231 | 1246 | 1277
| 8 | 1547 | 1595 | 1642 | 1689 | 1736 | 1783 | 1829 | 1852 | 1875 | 1921
| 9 | 2176 | 2242 | 2307 | 2373 | 2438 | 2502 | 2567 | 2599 | 2632 | 2696
| 10 | 2840 | 2925 | 3009 | 3093 | 3176 | 3259 | 3342 | 3384 | 3425 | 3508
| 11 | 3477 | 3578 | 3678 | 3767 | 3845 | 3922 | 3997 | 4035 | 4072 | 4146
| 12 | 4009 | 4097 | 4183 | 4246 | 4287 | 4324 | 4358 | 4375 | 4391 | 4423
| 13 | 4327 | 4369 | 4408 | 4434 | 4449 | 4461 | 4471 | 4475 | 4480 | 4488
| 14 | 4449 | 4460 | 4471 | 4479 | 4484 | 4488 | 4492 | 4493 | 4495 | 4500
| 15 | 4486 | 4489 | 4491 | 4493 | 4495 | 4500 | 4500 | 4500 | 4500 | 4500
| 16 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 17 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 18 | 4482 | 4482 | 4482 | 4482 | 4482 | 4482 | 4482 | 4482 | 4482 | 4482
| 19 | 4408 | 4408 | 4408 | 4408 | 4408 | 4408 | 4408 | 4408 | 4408 | 4408
| 20 | 4257 | 4257 | 4257 | 4257 | 4257 | 4257 | 4257 | 4257 | 4257 | 4257
| 21 | 4060 | 4060 | 4060 | 4060 | 4060 | 4060 | 4060 | 4060 | 4060 | 4060
| 22 | 3851 | 3851 | 3851 | 3851 | 3851 | 3851 | 3851 | 3851 | 3851 | 3851
| 23 | 3644 | 3644 | 3644 | 3644 | 3644 | 3644 | 3644 | 3644 | 3644 | 3644
| 24 | 3442 | 3442 | 3442 | 3442 | 3442 | 3442 | 3442 | 3442 | 3442 | 3442
| 25 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245
| 26 | 3053 | 3053 | 3053 | 3053 | 3053 | 3053 | 3053 | 3053 | 3053 | 3053
| 27 | 2866 | 2866 | 2866 | 2866 | 2866 | 2866 | 2866 | 2866 | 2866 | 2866
| 28 | 2686 | 2686 | 2686 | 2686 | 2686 | 2686 | 2686 | 2686 | 2686 | 2686
| 29 | 2518 | 2518 | 2518 | 2518 | 2518 | 2518 | 2518 | 2518 | 2518 | 2518
| 30 | 2377 | 2377 | 2377 | 2377 | 2377 | 2377 | 2377 | 2377 | 2377 | 2377

## Hoja4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
1.225
Wind Speed (m/s) | 0 | 0
| 1 | 0
| 2 | 0
| 3 | 0.845
| 4 | 0.849
| 5 | 0.85
| 6 | 0.851
| 7 | 0.852
| 8 | 0.842
| 9 | 0.789
| 10 | 0.696
| 11 | 0.581
| 12 | 0.454
| 13 | 0.347
| 14 | 0.271
| 15 | 0.218
| 16 | 0.178
| 17 | 0.148
| 18 | 0.125
| 19 | 0.105
| 20 | 0.088
| 21 | 0.073
| 22 | 0.061
| 23 | 0.051
| 24 | 0.043
| 25 | 0.037
| 26 | 0.031
| 27 | 0.027
| 28 | 0.023
| 29 | 0.02
| 30 | 0.017