## Sheet1
PROPERTIES
General
Name | Gamesa G132 3,0 IIA
Manufacturer | Enercon
Hub Height | 84 | 97 | 101.5 | 108 | 114 | 134 | 154 | 165
Power
Rated Power | 3465
Peak Power | 3465
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 132
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 3
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 25
Restart Wind Speed | 20
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -30
Low Temperature Restart | -20
High Temperature Shutdown | 45
High Temperature Restart | 45
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | II
Turbine SubClass | A
Values
Certification | IEC 3rd Edition
Vave | 9.8
Vref | 59.5
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 25.9906 | 26.6745 | 27.3585 | 28.0425 | 28.7264 | 29.5872 | 31.1429 | 32.2826 | 33 | 34.8517 | 35.7025 | 37 | 38.3858 | 39.1535
| 3.5 | 75.283 | 77.2642 | 79.2453 | 81.2264 | 83.2075 | 85.8028 | 88.5625 | 91.9565 | 94 | 97.5847 | 100.6612 | 103 | 106.7913 | 108.9272
| 4 | 124.5755 | 127.8538 | 131.1321 | 134.4104 | 137.6887 | 142.0183 | 145.9821 | 151.6304 | 155 | 160.3178 | 165.6198 | 169 | 175.1969 | 178.7008
| 4.5 | 224.9528 | 230.8726 | 236.7925 | 242.7123 | 248.6321 | 256.422 | 262.2812 | 272.4457 | 278.5 | 286.7797 | 295.0413 | 301.5 | 311.0236 | 317.2441
| 5 | 325.3302 | 333.8915 | 342.4528 | 351.0142 | 359.5755 | 370.8257 | 378.5804 | 393.2609 | 402 | 413.2415 | 424.4628 | 434 | 446.8504 | 455.7874
| 5.5 | 475 | 487.5 | 500 | 512.5 | 525 | 539.9656 | 549.3795 | 569.3478 | 582 | 596.9597 | 611.405 | 625 | 640.748 | 653.563
| 6 | 624.6698 | 641.1085 | 657.5472 | 673.9858 | 690.4245 | 709.1055 | 720.1786 | 745.4348 | 762 | 780.678 | 798.3471 | 816 | 834.6457 | 851.3386
| 6.5 | 824.0802 | 845.7665 | 867.4528 | 889.1392 | 910.8255 | 934.461 | 948.3973 | 980.7065 | 1002.5 | 1026.1335 | 1049.2562 | 1071.5 | 1095.4724 | 1117.3819
| 7 | 1023.4906 | 1050.4245 | 1077.3585 | 1104.2925 | 1131.2264 | 1159.8165 | 1176.6161 | 1215.9783 | 1243 | 1271.589 | 1300.1653 | 1327 | 1356.2992 | 1383.4252
| 7.5 | 1284.2925 | 1318.0896 | 1351.8868 | 1385.684 | 1419.4811 | 1454.2087 | 1475.3929 | 1523.6413 | 1557.5 | 1592.7225 | 1627.438 | 1661.5 | 1695.8661 | 1729.7835
| 8 | 1545.0943 | 1585.7547 | 1626.4151 | 1667.0755 | 1707.7358 | 1748.6009 | 1774.1696 | 1831.3043 | 1872 | 1913.8559 | 1954.7107 | 1996 | 2035.4331 | 2076.1417
| 8.5 | 1853.3962 | 1902.1698 | 1950.9434 | 1999.717 | 2048.4906 | 2094.2775 | 2120.6339 | 2184.4565 | 2233 | 2276.3136 | 2318.6777 | 2365 | 2399.1142 | 2447.0965
| 9 | 2161.6981 | 2218.5849 | 2275.4717 | 2332.3585 | 2389.2453 | 2439.9541 | 2467.0982 | 2537.6087 | 2594 | 2638.7712 | 2682.6446 | 2734 | 2762.7953 | 2818.0512
| 9.5 | 2437.7358 | 2501.8868 | 2566.0377 | 2630.1887 | 2694.3396 | 2738.2913 | 2754.1964 | 2817.8804 | 2880.5 | 2915.0953 | 2947.9339 | 2996 | 3004.9213 | 3065.0197
| 10 | 2713.7736 | 2785.1887 | 2856.6038 | 2928.0189 | 2999.434 | 3036.6284 | 3041.2946 | 3098.1522 | 3167 | 3191.4195 | 3213.2231 | 3258 | 3247.0472 | 3311.9882
| 10.5 | 2870.6132 | 2946.1557 | 3021.6981 | 3097.2406 | 3172.783 | 3195.906 | 3186.3036 | 3232.1739 | 3304 | 3316.3877 | 3326.281 | 3366.5 | 3340.5512 | 3407.3622
| 11 | 3027.4528 | 3107.1226 | 3186.7925 | 3266.4623 | 3346.1321 | 3355.1835 | 3331.3125 | 3366.1957 | 3441 | 3441.3559 | 3439.3388 | 3475 | 3434.0551 | 3502.7362
| 11.5 | 3084.8113 | 3165.9906 | 3247.1698 | 3328.3491 | 3409.5283 | 3410.4128 | 3378.5134 | 3407.2826 | 3483 | 3477.7013 | 3471.5702 | 3504.5 | 3458.1693 | 3527.3327
| 12 | 3142.1698 | 3224.8585 | 3307.5472 | 3390.2358 | 3472.9245 | 3465.6422 | 3425.7143 | 3448.3696 | 3525 | 3514.0466 | 3503.8017 | 3534 | 3482.2835 | 3551.9291
| 12.5 | 3157.4057 | 3240.4953 | 3323.5849 | 3406.6745 | 3489.7642 | 3479.4495 | 3437.3929 | 3458.1522 | 3535 | 3522.5106 | 3510.7438 | 3540.5 | 3487.2047 | 3556.9488
| 13 | 3172.6415 | 3256.1321 | 3339.6226 | 3423.1132 | 3506.6038 | 3493.2569 | 3449.0714 | 3467.9348 | 3545 | 3530.9746 | 3517.686 | 3547 | 3492.126 | 3561.9685
| 13.5 | 3176.2264 | 3259.8113 | 3343.3962 | 3426.9811 | 3510.566 | 3496.7087 | 3451.5045 | 3469.8913 | 3547 | 3532.4682 | 3518.6777 | 3548.5 | 3493.1102 | 3562.9724
| 14 | 3179.8113 | 3263.4906 | 3347.1698 | 3430.8491 | 3514.5283 | 3500.1606 | 3453.9375 | 3471.8478 | 3549 | 3533.9619 | 3519.6694 | 3550 | 3494.0945 | 3563.9764
| 14.5 | 3180.7075 | 3264.4104 | 3348.1132 | 3431.816 | 3515.5189 | 3500.6537 | 3454.4241 | 3472.337 | 3549.5 | 3534.4597 | 3520.1653 | 3550 | 3494.0945 | 3563.9764
| 15 | 3181.6038 | 3265.3302 | 3349.0566 | 3432.783 | 3516.5094 | 3501.1468 | 3454.9107 | 3472.8261 | 3550 | 3534.9576 | 3520.6612 | 3550 | 3494.0945 | 3563.9764
| 15.5 | 3181.6038 | 3265.3302 | 3349.0566 | 3432.783 | 3516.5094 | 3501.1468 | 3454.9107 | 3472.8261 | 3550 | 3534.9576 | 3520.6612 | 3550 | 3494.0945 | 3563.9764
| 16 | 3181.6038 | 3265.3302 | 3349.0566 | 3432.783 | 3516.5094 | 3501.1468 | 3454.9107 | 3472.8261 | 3550 | 3534.9576 | 3520.6612 | 3550 | 3494.0945 | 3563.9764
| 16.5 | 3181.1557 | 3264.8703 | 3348.5849 | 3432.2995 | 3516.0142 | 3500.6537 | 3454.4241 | 3472.337 | 3549.5 | 3534.4597 | 3520.1653 | 3549.5 | 3493.6024 | 3563.4744
| 17 | 3180.7075 | 3264.4104 | 3348.1132 | 3431.816 | 3515.5189 | 3500.1606 | 3453.9375 | 3471.8478 | 3549 | 3533.9619 | 3519.6694 | 3549 | 3493.1102 | 3562.9724
| 17.5 | 3178.467 | 3262.1108 | 3345.7547 | 3429.3986 | 3513.0425 | 3497.695 | 3451.5045 | 3469.4022 | 3546.5 | 3531.4725 | 3517.1901 | 3546.5 | 3490.6496 | 3560.4626
| 18 | 3176.2264 | 3259.8113 | 3343.3962 | 3426.9811 | 3510.566 | 3495.2294 | 3449.0714 | 3466.9565 | 3544 | 3528.9831 | 3514.7107 | 3544 | 3488.189 | 3557.9528
| 18.5 | 3167.2642 | 3250.6132 | 3333.9623 | 3417.3113 | 3500.6604 | 3485.367 | 3439.3393 | 3457.1739 | 3534 | 3519.0254 | 3504.7934 | 3534 | 3478.3465 | 3547.9134
| 19 | 3158.3019 | 3241.4151 | 3324.5283 | 3407.6415 | 3490.7547 | 3475.5046 | 3429.6071 | 3447.3913 | 3524 | 3509.0678 | 3494.876 | 3524 | 3468.5039 | 3537.874
| 19.5 | 3136.7925 | 3219.3396 | 3301.8868 | 3384.434 | 3466.9811 | 3451.8349 | 3406.25 | 3423.913 | 3500 | 3485.1695 | 3471.0744 | 3500 | 3444.8819 | 3513.7795
| 20 | 3115.283 | 3197.2642 | 3279.2453 | 3361.2264 | 3443.2075 | 3428.1651 | 3382.8929 | 3400.4348 | 3476 | 3461.2712 | 3447.2727 | 3476 | 3421.2598 | 3489.685
| 20.5 | 3077.6415 | 3158.6321 | 3239.6226 | 3320.6132 | 3401.6038 | 3386.7431 | 3342.0179 | 3359.3478 | 3434 | 3419.4492 | 3405.6198 | 3434 | 3379.9213 | 3447.5197
| 21 | 3040 | 3120 | 3200 | 3280 | 3360 | 3345.3211 | 3301.1429 | 3318.2609 | 3392 | 3377.6271 | 3363.9669 | 3392 | 3338.5827 | 3405.3543
| 21.5 | 2987.5708 | 3066.191 | 3144.8113 | 3223.4316 | 3302.0519 | 3287.6261 | 3244.2098 | 3261.0326 | 3333.5 | 3319.375 | 3305.9504 | 3333.5 | 3281.0039 | 3346.624
| 22 | 2935.1415 | 3012.3821 | 3089.6226 | 3166.8632 | 3244.1038 | 3229.9312 | 3187.2768 | 3203.8043 | 3275 | 3261.1229 | 3247.9339 | 3275 | 3223.4252 | 3287.8937
| 22.5 | 1467.5708 | 1506.191 | 1544.8113 | 1583.4316 | 1622.0519 | 1614.9656 | 1593.6384 | 1601.9022 | 1637.5 | 1630.5614 | 1623.9669 | 1637.5 | 1611.7126 | 1643.9469

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.79137 | 0.81219 | 0.83302 | 0.85384 | 0.87467 | 0.883 | 0.883 | 0.883 | 0.883 | 0.883 | 0.883 | 0.883 | 0.883 | 0.883
| 3.5 | 0.77075 | 0.79104 | 0.81132 | 0.8316 | 0.85189 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86
| 4 | 0.75014 | 0.76988 | 0.78962 | 0.80936 | 0.8291 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837
| 4.5 | 0.7255 | 0.74459 | 0.76368 | 0.78277 | 0.80186 | 0.8095 | 0.8095 | 0.8095 | 0.8095 | 0.81 | 0.81 | 0.8095 | 0.8095 | 0.8095
| 5 | 0.70085 | 0.71929 | 0.73774 | 0.75618 | 0.77462 | 0.782 | 0.782 | 0.782 | 0.782 | 0.782 | 0.782 | 0.782 | 0.782 | 0.782
| 5.5 | 0.68472 | 0.70274 | 0.72075 | 0.73877 | 0.75679 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764
| 6 | 0.66858 | 0.68618 | 0.70377 | 0.72137 | 0.73896 | 0.746 | 0.746 | 0.746 | 0.746 | 0.746 | 0.746 | 0.746 | 0.746 | 0.746
| 6.5 | 0.66679 | 0.68434 | 0.70189 | 0.71943 | 0.73698 | 0.744 | 0.744 | 0.744 | 0.744 | 0.744 | 0.744 | 0.744 | 0.744 | 0.744
| 7 | 0.665 | 0.6825 | 0.7 | 0.7175 | 0.735 | 0.742 | 0.742 | 0.742 | 0.742 | 0.742 | 0.742 | 0.742 | 0.742 | 0.742
| 7.5 | 0.66142 | 0.67882 | 0.69623 | 0.71363 | 0.73104 | 0.738 | 0.738 | 0.738 | 0.738 | 0.738 | 0.738 | 0.738 | 0.738 | 0.738
| 8 | 0.65783 | 0.67514 | 0.69245 | 0.70976 | 0.72708 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734
| 8.5 | 0.64215 | 0.65904 | 0.67594 | 0.69284 | 0.70974 | 0.7165 | 0.70272 | 0.7155 | 0.7145 | 0.714 | 0.713 | 0.712 | 0.711 | 0.71
| 9 | 0.62646 | 0.64295 | 0.65943 | 0.67592 | 0.69241 | 0.699 | 0.68455 | 0.697 | 0.695 | 0.694 | 0.692 | 0.69 | 0.688 | 0.685
| 9.5 | 0.59196 | 0.60754 | 0.62311 | 0.63869 | 0.65427 | 0.6605 | 0.64232 | 0.65 | 0.65 | 0.648 | 0.643 | 0.638 | 0.634 | 0.629
| 10 | 0.55745 | 0.57212 | 0.58679 | 0.60146 | 0.61613 | 0.622 | 0.60009 | 0.609 | 0.605 | 0.6 | 0.599 | 0.586 | 0.579 | 0.57
| 10.5 | 0.50726 | 0.52061 | 0.53396 | 0.54731 | 0.56066 | 0.566 | 0.54067 | 0.547 | 0.5425 | 0.539 | 0.53 | 0.52 | 0.51 | 0.501
| 11 | 0.45708 | 0.4691 | 0.48113 | 0.49316 | 0.50519 | 0.51 | 0.48125 | 0.485 | 0.48 | 0.475 | 0.462 | 0.454 | 0.442 | 0.432
| 11.5 | 0.40644 | 0.41713 | 0.42783 | 0.43853 | 0.44922 | 0.4535 | 0.42527 | 0.427 | 0.423 | 0.42 | 0.41 | 0.398 | 0.39 | 0.38
| 12 | 0.3558 | 0.36517 | 0.37453 | 0.38389 | 0.39325 | 0.397 | 0.36929 | 0.369 | 0.366 | 0.36 | 0.351 | 0.342 | 0.332 | 0.325
| 12.5 | 0.31502 | 0.32331 | 0.3316 | 0.33989 | 0.34818 | 0.3515 | 0.32656 | 0.329 | 0.3235 | 0.32 | 0.312 | 0.3025 | 0.294 | 0.199
| 13 | 0.27425 | 0.28146 | 0.28868 | 0.2959 | 0.30311 | 0.306 | 0.28384 | 0.287 | 0.281 | 0.279 | 0.27 | 0.263 | 0.255 | 0.25
| 13.5 | 0.24467 | 0.25111 | 0.25755 | 0.26399 | 0.27042 | 0.273 | 0.25339 | 0.255 | 0.251 | 0.249 | 0.242 | 0.235 | 0.23 | 0.225
| 14 | 0.21509 | 0.22075 | 0.22642 | 0.23208 | 0.23774 | 0.24 | 0.22295 | 0.225 | 0.221 | 0.219 | 0.213 | 0.207 | 0.203 | 0.198
| 14.5 | 0.19403 | 0.19914 | 0.20425 | 0.20935 | 0.21446 | 0.2165 | 0.20134 | 0.204 | 0.1995 | 0.198 | 0.192 | 0.187 | 0.183 | 0.18
| 15 | 0.17297 | 0.17752 | 0.18208 | 0.18663 | 0.19118 | 0.193 | 0.17973 | 0.18 | 0.178 | 0.176 | 0.17 | 0.167 | 0.163 | 0.159
| 15.5 | 0.15729 | 0.16143 | 0.16557 | 0.16971 | 0.17384 | 0.1755 | 0.16353 | 0.164 | 0.162 | 0.16 | 0.156 | 0.152 | 0.149 | 0.145
| 16 | 0.1416 | 0.14533 | 0.14906 | 0.15278 | 0.15651 | 0.158 | 0.14732 | 0.148 | 0.146 | 0.144 | 0.14 | 0.137 | 0.135 | 0.13
| 16.5 | 0.1295 | 0.13291 | 0.13632 | 0.13973 | 0.14314 | 0.1445 | 0.13504 | 0.135 | 0.134 | 0.133 | 0.13 | 0.1255 | 0.124 | 0.12
| 17 | 0.11741 | 0.1205 | 0.12358 | 0.12667 | 0.12976 | 0.131 | 0.12277 | 0.123 | 0.122 | 0.12 | 0.118 | 0.114 | 0.112 | 0.11
| 17.5 | 0.10844 | 0.1113 | 0.11415 | 0.117 | 0.11986 | 0.121 | 0.11295 | 0.114 | 0.1125 | 0.112 | 0.108 | 0.1055 | 0.104 | 0.1
| 18 | 0.099481 | 0.1021 | 0.10472 | 0.10733 | 0.10995 | 0.111 | 0.10312 | 0.104 | 0.103 | 0.102 | 0.099 | 0.097 | 0.095 | 0.09
| 18.5 | 0.091863 | 0.094281 | 0.096698 | 0.099116 | 0.10153 | 0.1025 | 0.095268 | 0.096 | 0.095 | 0.094 | 0.092 | 0.0895 | 0.088 | 0.085
| 19 | 0.084245 | 0.086462 | 0.088679 | 0.090896 | 0.093113 | 0.094 | 0.087411 | 0.088 | 0.087 | 0.086 | 0.084 | 0.082 | 0.08 | 0.079
| 19.5 | 0.077972 | 0.080024 | 0.082075 | 0.084127 | 0.086179 | 0.087 | 0.081027 | 0.82 | 0.0805 | 0.08 | 0.078 | 0.076 | 0.074 | 0.072
| 20 | 0.071698 | 0.073585 | 0.075472 | 0.077358 | 0.079245 | 0.08 | 0.074643 | 0.075 | 0.074 | 0.073 | 0.071 | 0.07 | 0.068 | 0.067
| 20.5 | 0.066321 | 0.068066 | 0.069811 | 0.071557 | 0.073302 | 0.074 | 0.06875 | 0.069 | 0.0685 | 0.068 | 0.066 | 0.065 | 0.063 | 0.062
| 21 | 0.060943 | 0.062547 | 0.064151 | 0.065755 | 0.067358 | 0.068 | 0.062857 | 0.063 | 0.063 | 0.062 | 0.061 | 0.06 | 0.058 | 0.056
| 21.5 | 0.056014 | 0.057488 | 0.058962 | 0.060436 | 0.06191 | 0.0625 | 0.058438 | 0.058 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053
| 22 | 0.051085 | 0.052429 | 0.053774 | 0.055118 | 0.056462 | 0.057 | 0.054018 | 0.053 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.047
| 22.5 | 0.047052 | 0.04829 | 0.049528 | 0.050767 | 0.052005 | 0.0525 | 0.049598 | 0.049 | 0.049 | 0.048 | 0.047 | 0.0465 | 0.045 | 0.043