## Sheet1
PROPERTIES
General
Name | Gamesa SG 4.7-155 -MOD 4,2MW
Manufacturer | Gamesa
Hub Height | 90 | 102.5 | 120.5
Power
Rated Power | 4200
Peak Power | 4200
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 155
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 27
Restart Wind Speed | 24
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -30
Low Temperature Restart | -20
High Temperature Shutdown | 50
High Temperature Restart | 45
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | III
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 37.5
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.94 | 0.97 | 1 | 1.03 | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.24 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 17 | 19 | 21 | 24 | 27 | 30 | 33 | 36 | 39 | 42 | 44 | 45 | 48
| 3.5 | 75 | 80 | 84 | 89 | 94 | 99 | 104 | 109 | 114 | 119 | 122 | 124 | 129
| 4 | 166 | 174 | 182 | 190 | 198 | 206 | 214 | 223 | 231 | 239 | 243 | 247 | 255
| 4.5 | 284 | 296 | 308 | 320 | 332 | 345 | 357 | 369 | 381 | 393 | 399 | 405 | 417
| 5 | 431 | 448 | 465 | 482 | 499 | 516 | 532 | 549 | 566 | 583 | 592 | 600 | 617
| 5.5 | 609 | 632 | 655 | 678 | 700 | 723 | 745 | 768 | 791 | 813 | 824 | 836 | 858
| 6 | 823 | 853 | 882 | 912 | 941 | 970 | 999 | 1029 | 1058 | 1087 | 1101 | 1116 | 1145
| 6.5 | 1075 | 1113 | 1150 | 1187 | 1224 | 1261 | 1298 | 1335 | 1372 | 1408 | 1427 | 1445 | 1482
| 7 | 1367 | 1414 | 1460 | 1506 | 1552 | 1598 | 1644 | 1690 | 1735 | 1781 | 1804 | 1827 | 1873
| 7.5 | 1701 | 1757 | 1814 | 1870 | 1927 | 1983 | 2039 | 2095 | 2151 | 2207 | 2235 | 2263 | 2318
| 8 | 2075 | 2143 | 2211 | 2279 | 2347 | 2414 | 2481 | 2547 | 2613 | 2677 | 2710 | 2741 | 2804
| 8.5 | 2481 | 2561 | 2640 | 2719 | 2796 | 2872 | 2946 | 3018 | 3088 | 3156 | 3189 | 3221 | 3284
| 9 | 2899 | 2988 | 3074 | 3158 | 3238 | 3315 | 3388 | 3456 | 3521 | 3582 | 3611 | 3639 | 3692
| 9.5 | 3297 | 3387 | 3472 | 3550 | 3624 | 3691 | 3753 | 3808 | 3859 | 3904 | 3926 | 3945 | 3982
| 10 | 3642 | 3723 | 3795 | 3859 | 3916 | 3966 | 4009 | 4045 | 4076 | 4101 | 4111 | 4120 | 4136
| 10.5 | 3910 | 3972 | 4023 | 4066 | 4100 | 4124 | 4142 | 4155 | 4165 | 4172 | 4175 | 4177 | 4181
| 11 | 4087 | 4121 | 4145 | 4160 | 4170 | 4177 | 4182 | 4185 | 4188 | 4190 | 4191 | 4192 | 4193
| 11.5 | 4165 | 4175 | 4182 | 4186 | 4189 | 4191 | 4193 | 4194 | 4195 | 4196 | 4197 | 4197 | 4198
| 12 | 4187 | 4190 | 4192 | 4194 | 4196 | 4197 | 4197 | 4198 | 4199 | 4199 | 4199 | 4199 | 4200
| 12.5 | 4194 | 4196 | 4197 | 4198 | 4199 | 4199 | 4199 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 13 | 4198 | 4199 | 4199 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 13.5 | 4199 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 14 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 14.5 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 15 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 15.5 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 16 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 16.5 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 17 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 17.5 | 4199 | 4199 | 4199 | 4199 | 4199 | 4199 | 4199 | 4199 | 4199 | 4199 | 4199 | 4199 | 4199
| 18 | 4198 | 4198 | 4198 | 4198 | 4198 | 4198 | 4198 | 4198 | 4198 | 4198 | 4198 | 4198 | 4198
| 18.5 | 4197 | 4197 | 4197 | 4197 | 4197 | 4197 | 4197 | 4197 | 4197 | 4197 | 4197 | 4197 | 4197
| 19 | 4194 | 4194 | 4194 | 4194 | 4194 | 4194 | 4194 | 4194 | 4194 | 4194 | 4194 | 4194 | 4194
| 19.5 | 4190 | 4190 | 4190 | 4190 | 4190 | 4190 | 4190 | 4190 | 4190 | 4190 | 4190 | 4190 | 4190
| 20 | 4184 | 4184 | 4184 | 4184 | 4184 | 4184 | 4184 | 4184 | 4184 | 4184 | 4184 | 4184 | 4184
| 20.5 | 4177 | 4177 | 4177 | 4177 | 4177 | 4177 | 4177 | 4177 | 4177 | 4177 | 4177 | 4177 | 4177
| 21 | 4168 | 4168 | 4168 | 4168 | 4168 | 4168 | 4168 | 4168 | 4168 | 4168 | 4168 | 4168 | 4168
| 21.5 | 4156 | 4156 | 4156 | 4156 | 4156 | 4156 | 4156 | 4156 | 4156 | 4156 | 4156 | 4156 | 4156
| 22 | 4133 | 4133 | 4133 | 4133 | 4133 | 4133 | 4133 | 4133 | 4133 | 4133 | 4133 | 4133 | 4133
| 22.5 | 4091 | 4091 | 4091 | 4091 | 4091 | 4091 | 4091 | 4091 | 4091 | 4091 | 4091 | 4091 | 4091
| 23 | 4045 | 4045 | 4045 | 4045 | 4045 | 4045 | 4045 | 4045 | 4045 | 4045 | 4045 | 4045 | 4045
| 23.5 | 4001 | 4001 | 4001 | 4001 | 4001 | 4001 | 4001 | 4001 | 4001 | 4001 | 4001 | 4001 | 4001
| 24 | 3959 | 3959 | 3959 | 3959 | 3959 | 3959 | 3959 | 3959 | 3959 | 3959 | 3959 | 3959 | 3959
| 24.5 | 3922 | 3922 | 3922 | 3922 | 3922 | 3922 | 3922 | 3922 | 3922 | 3922 | 3922 | 3922 | 3922
| 25 | 3888 | 3888 | 3888 | 3888 | 3888 | 3888 | 3888 | 3888 | 3888 | 3888 | 3888 | 3888 | 3888
| 25.5 | 3860 | 3860 | 3860 | 3860 | 3860 | 3860 | 3860 | 3860 | 3860 | 3860 | 3860 | 3860 | 3860
| 26 | 3834 | 3834 | 3834 | 3834 | 3834 | 3834 | 3834 | 3834 | 3834 | 3834 | 3834 | 3834 | 3834
| 26.5 | 3812 | 3812 | 3812 | 3812 | 3812 | 3812 | 3812 | 3812 | 3812 | 3812 | 3812 | 3812 | 3812
| 27 | 3791 | 3791 | 3791 | 3791 | 3791 | 3791 | 3791 | 3791 | 3791 | 3791 | 3791 | 3791 | 3791

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.94 | 0.97 | 1 | 1.03 | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.24 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115
| 3.5 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532
| 4 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8335
| 4.5 | 0.8196 | 0.8197 | 0.8198 | 0.8198 | 0.8199 | 0.82 | 0.82 | 0.8201 | 0.8201 | 0.8202 | 0.8202 | 0.8202 | 0.8202
| 5 | 0.8072 | 0.8077 | 0.8081 | 0.8084 | 0.8087 | 0.809 | 0.8093 | 0.8095 | 0.8097 | 0.8098 | 0.8098 | 0.8099 | 0.81
| 5.5 | 0.8014 | 0.8021 | 0.8027 | 0.8031 | 0.8035 | 0.8039 | 0.8043 | 0.8046 | 0.8048 | 0.805 | 0.805 | 0.8051 | 0.8053
| 6 | 0.8018 | 0.8023 | 0.8028 | 0.8031 | 0.8034 | 0.8037 | 0.804 | 0.8042 | 0.8044 | 0.8046 | 0.8047 | 0.8047 | 0.8049
| 6.5 | 0.8038 | 0.8041 | 0.8044 | 0.8046 | 0.8048 | 0.805 | 0.8051 | 0.8053 | 0.8054 | 0.8055 | 0.8055 | 0.8056 | 0.8057
| 7 | 0.8052 | 0.8054 | 0.8055 | 0.8057 | 0.8058 | 0.8059 | 0.806 | 0.8061 | 0.8061 | 0.8062 | 0.8062 | 0.8062 | 0.8063
| 7.5 | 0.8049 | 0.805 | 0.8051 | 0.8051 | 0.8052 | 0.8052 | 0.8052 | 0.8052 | 0.8051 | 0.805 | 0.8049 | 0.8048 | 0.8044
| 8 | 0.799 | 0.799 | 0.799 | 0.7989 | 0.7988 | 0.7985 | 0.7981 | 0.7975 | 0.7967 | 0.7955 | 0.7949 | 0.7941 | 0.7923
| 8.5 | 0.7813 | 0.781 | 0.7805 | 0.7799 | 0.7788 | 0.7774 | 0.7755 | 0.773 | 0.7698 | 0.7661 | 0.7642 | 0.7617 | 0.7566
| 9 | 0.7478 | 0.7465 | 0.7447 | 0.7421 | 0.7388 | 0.7348 | 0.7297 | 0.7238 | 0.7171 | 0.7096 | 0.7058 | 0.7014 | 0.6924
| 9.5 | 0.6992 | 0.6956 | 0.691 | 0.6853 | 0.6786 | 0.671 | 0.6623 | 0.6527 | 0.6423 | 0.6314 | 0.6259 | 0.6199 | 0.6082
| 10 | 0.6392 | 0.6324 | 0.6243 | 0.6151 | 0.6049 | 0.594 | 0.5822 | 0.5699 | 0.5572 | 0.5441 | 0.5376 | 0.5308 | 0.5174
| 10.5 | 0.5727 | 0.5625 | 0.5513 | 0.5392 | 0.5264 | 0.5129 | 0.499 | 0.4852 | 0.4716 | 0.4584 | 0.452 | 0.4456 | 0.4334
| 11 | 0.5043 | 0.4912 | 0.4773 | 0.4632 | 0.4492 | 0.4356 | 0.4224 | 0.4099 | 0.3979 | 0.3865 | 0.3811 | 0.3758 | 0.3656
| 11.5 | 0.4367 | 0.4225 | 0.4087 | 0.3955 | 0.383 | 0.3711 | 0.3599 | 0.3493 | 0.3393 | 0.3299 | 0.3254 | 0.321 | 0.3126
| 12 | 0.3766 | 0.3637 | 0.3516 | 0.3403 | 0.3296 | 0.3196 | 0.3101 | 0.3013 | 0.2929 | 0.285 | 0.2812 | 0.2776 | 0.2705
| 12.5 | 0.3269 | 0.3158 | 0.3055 | 0.2958 | 0.2867 | 0.2782 | 0.2702 | 0.2626 | 0.2555 | 0.2489 | 0.2457 | 0.2425 | 0.2366
| 13 | 0.2862 | 0.2766 | 0.2677 | 0.2594 | 0.2517 | 0.2443 | 0.2375 | 0.231 | 0.225 | 0.2192 | 0.2165 | 0.2138 | 0.2087
| 13.5 | 0.2526 | 0.2443 | 0.2366 | 0.2294 | 0.2227 | 0.2164 | 0.2104 | 0.2048 | 0.1996 | 0.1946 | 0.1922 | 0.1899 | 0.1854
| 14 | 0.2245 | 0.2173 | 0.2106 | 0.2043 | 0.1984 | 0.1929 | 0.1877 | 0.1828 | 0.1782 | 0.1739 | 0.1718 | 0.1697 | 0.1658
| 14.5 | 0.2008 | 0.1945 | 0.1886 | 0.1831 | 0.1779 | 0.173 | 0.1685 | 0.1642 | 0.1601 | 0.1562 | 0.1544 | 0.1526 | 0.1491
| 15 | 0.1806 | 0.175 | 0.1698 | 0.1649 | 0.1603 | 0.156 | 0.152 | 0.1481 | 0.1445 | 0.1411 | 0.1394 | 0.1378 | 0.1348
| 15.5 | 0.1633 | 0.1583 | 0.1536 | 0.1493 | 0.1452 | 0.1413 | 0.1377 | 0.1343 | 0.1311 | 0.128 | 0.1265 | 0.1251 | 0.1223
| 16 | 0.1483 | 0.1438 | 0.1396 | 0.1357 | 0.132 | 0.1286 | 0.1253 | 0.1223 | 0.1193 | 0.1166 | 0.1153 | 0.114 | 0.1115
| 16.5 | 0.1352 | 0.1311 | 0.1274 | 0.1239 | 0.1206 | 0.1174 | 0.1145 | 0.1117 | 0.1091 | 0.1066 | 0.1054 | 0.1042 | 0.102
| 17 | 0.1237 | 0.12 | 0.1166 | 0.1135 | 0.1105 | 0.1076 | 0.105 | 0.1025 | 0.1001 | 0.0978 | 0.0967 | 0.0957 | 0.0936
| 17.5 | 0.1136 | 0.1103 | 0.1072 | 0.1043 | 0.1015 | 0.099 | 0.0966 | 0.0943 | 0.0921 | 0.09 | 0.0891 | 0.0881 | 0.0862
| 18 | 0.1046 | 0.1016 | 0.0987 | 0.0961 | 0.0936 | 0.0913 | 0.0891 | 0.087 | 0.085 | 0.0831 | 0.0822 | 0.0813 | 0.0797
| 18.5 | 0.0966 | 0.0938 | 0.0912 | 0.0888 | 0.0866 | 0.0844 | 0.0824 | 0.0805 | 0.0787 | 0.0769 | 0.0761 | 0.0753 | 0.0738
| 19 | 0.0894 | 0.0869 | 0.0845 | 0.0823 | 0.0802 | 0.0782 | 0.0764 | 0.0746 | 0.073 | 0.0714 | 0.0706 | 0.0699 | 0.0685
| 19.5 | 0.0829 | 0.0806 | 0.0785 | 0.0764 | 0.0745 | 0.0727 | 0.071 | 0.0694 | 0.0678 | 0.0664 | 0.0657 | 0.065 | 0.0637
| 20 | 0.0771 | 0.075 | 0.073 | 0.0711 | 0.0693 | 0.0677 | 0.0661 | 0.0646 | 0.0632 | 0.0619 | 0.0612 | 0.0606 | 0.0594
| 20.5 | 0.0719 | 0.0699 | 0.068 | 0.0663 | 0.0647 | 0.0631 | 0.0617 | 0.0603 | 0.059 | 0.0577 | 0.0571 | 0.0566 | 0.0554
| 21 | 0.0671 | 0.0653 | 0.0635 | 0.0619 | 0.0604 | 0.059 | 0.0576 | 0.0564 | 0.0551 | 0.054 | 0.0534 | 0.0529 | 0.0519
| 21.5 | 0.0627 | 0.061 | 0.0594 | 0.0579 | 0.0565 | 0.0552 | 0.054 | 0.0528 | 0.0517 | 0.0506 | 0.0501 | 0.0496 | 0.0486
| 22 | 0.0586 | 0.0571 | 0.0556 | 0.0542 | 0.0529 | 0.0517 | 0.0505 | 0.0494 | 0.0484 | 0.0474 | 0.0469 | 0.0464 | 0.0455
| 22.5 | 0.0547 | 0.0533 | 0.0519 | 0.0506 | 0.0494 | 0.0483 | 0.0472 | 0.0462 | 0.0452 | 0.0443 | 0.0438 | 0.0434 | 0.0426
| 23 | 0.0511 | 0.0498 | 0.0485 | 0.0473 | 0.0462 | 0.0451 | 0.0441 | 0.0432 | 0.0423 | 0.0414 | 0.041 | 0.0406 | 0.0399
| 23.5 | 0.0479 | 0.0466 | 0.0454 | 0.0443 | 0.0433 | 0.0423 | 0.0414 | 0.0405 | 0.0397 | 0.0389 | 0.0385 | 0.0381 | 0.0374
| 24 | 0.045 | 0.0438 | 0.0427 | 0.0416 | 0.0407 | 0.0398 | 0.0389 | 0.0381 | 0.0373 | 0.0366 | 0.0362 | 0.0359 | 0.0352
| 24.5 | 0.0424 | 0.0413 | 0.0402 | 0.0393 | 0.0383 | 0.0375 | 0.0367 | 0.0359 | 0.0352 | 0.0345 | 0.0342 | 0.0338 | 0.0332
| 25 | 0.04 | 0.039 | 0.038 | 0.0371 | 0.0363 | 0.0355 | 0.0347 | 0.034 | 0.0333 | 0.0326 | 0.0323 | 0.032 | 0.0314
| 25.5 | 0.0379 | 0.037 | 0.0361 | 0.0352 | 0.0344 | 0.0336 | 0.0329 | 0.0322 | 0.0316 | 0.031 | 0.0307 | 0.0304 | 0.0299
| 26 | 0.0361 | 0.0351 | 0.0343 | 0.0335 | 0.0327 | 0.032 | 0.0313 | 0.0306 | 0.03 | 0.0295 | 0.0292 | 0.0289 | 0.0284
| 26.5 | 0.0343 | 0.0335 | 0.0327 | 0.0319 | 0.0312 | 0.0305 | 0.0298 | 0.0292 | 0.0286 | 0.0281 | 0.0278 | 0.0276 | 0.0271
| 27 | 0.0328 | 0.0319 | 0.0311 | 0.0304 | 0.0297 | 0.0291 | 0.0285 | 0.0279 | 0.0273 | 0.0268 | 0.0266 | 0.0263 | 0.0258