## Sheet1
PROPERTIES
General
Name | Gamesa SG 4.7-155 -MOD 4,7MW
Manufacturer | Gamesa
Hub Height | 90 | 102.5 | 120.5
Power
Rated Power | 4700
Peak Power | 4700
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 155
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 27
Restart Wind Speed | 24
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -30
Low Temperature Restart | -20
High Temperature Shutdown | 50
High Temperature Restart | 45
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | III
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 37.5
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.24 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 27 | 30 | 33 | 36 | 39 | 42 | 44 | 45 | 48
| 4 | 198 | 206 | 214 | 223 | 231 | 239 | 243 | 247 | 255
| 5 | 499 | 516 | 532 | 549 | 566 | 583 | 592 | 600 | 617
| 6 | 941 | 970 | 999 | 1029 | 1058 | 1087 | 1101 | 1116 | 1145
| 7 | 1552 | 1598 | 1644 | 1690 | 1736 | 1781 | 1804 | 1827 | 1873
| 8 | 2348 | 2416 | 2484 | 2551 | 2619 | 2686 | 2719 | 2752 | 2819
| 9 | 3273 | 3361 | 3446 | 3529 | 3609 | 3686 | 3723 | 3760 | 3829
| 10 | 4096 | 4174 | 4244 | 4308 | 4364 | 4415 | 4438 | 4460 | 4499
| 11 | 4577 | 4610 | 4633 | 4650 | 4662 | 4671 | 4674 | 4677 | 4681
| 12 | 4686 | 4689 | 4692 | 4693 | 4695 | 4696 | 4696 | 4697 | 4697
| 13 | 4698 | 4698 | 4699 | 4699 | 4700 | 4700 | 4700 | 4700 | 4700
| 14 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 15 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 16 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 17 | 4699 | 4699 | 4699 | 4699 | 4699 | 4699 | 4699 | 4699 | 4699
| 18 | 4695 | 4695 | 4695 | 4695 | 4695 | 4695 | 4695 | 4695 | 4695
| 19 | 4683 | 4683 | 4683 | 4683 | 4683 | 4683 | 4683 | 4683 | 4683
| 20 | 4656 | 4656 | 4656 | 4656 | 4656 | 4656 | 4656 | 4656 | 4656
| 21 | 4549 | 4549 | 4549 | 4549 | 4549 | 4549 | 4549 | 4549 | 4549
| 22 | 4375 | 4375 | 4375 | 4375 | 4375 | 4375 | 4375 | 4375 | 4375
| 23 | 4207 | 4207 | 4207 | 4207 | 4207 | 4207 | 4207 | 4207 | 4207
| 24 | 4064 | 4064 | 4064 | 4064 | 4064 | 4064 | 4064 | 4064 | 4064
| 25 | 3956 | 3956 | 3956 | 3956 | 3956 | 3956 | 3956 | 3956 | 3956
| 26 | 3878 | 3878 | 3878 | 3878 | 3878 | 3878 | 3878 | 3878 | 3878
| 27 | 3821 | 3821 | 3821 | 3821 | 3821 | 3821 | 3821 | 3821 | 3821

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
| 10 | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.24 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115
| 4 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8335
| 5 | 0.8087 | 0.809 | 0.8093 | 0.8095 | 0.8097 | 0.8098 | 0.8098 | 0.8099 | 0.81
| 6 | 0.8034 | 0.8037 | 0.804 | 0.8042 | 0.8044 | 0.8046 | 0.8047 | 0.8047 | 0.8049
| 7 | 0.8058 | 0.8059 | 0.806 | 0.8061 | 0.8062 | 0.8062 | 0.8063 | 0.8063 | 0.8064
| 8 | 0.7992 | 0.7992 | 0.7991 | 0.7991 | 0.799 | 0.7987 | 0.7986 | 0.7984 | 0.7979
| 9 | 0.7476 | 0.7463 | 0.7445 | 0.7422 | 0.7392 | 0.7357 | 0.7336 | 0.7315 | 0.7265
| 10 | 0.6373 | 0.6308 | 0.6234 | 0.6151 | 0.606 | 0.5963 | 0.5912 | 0.5861 | 0.5754
| 11 | 0.5007 | 0.489 | 0.4767 | 0.4643 | 0.4519 | 0.4397 | 0.4338 | 0.4279 | 0.4165
| 12 | 0.3738 | 0.3625 | 0.3518 | 0.3416 | 0.332 | 0.3228 | 0.3185 | 0.3142 | 0.3061
| 13 | 0.2842 | 0.2758 | 0.2679 | 0.2604 | 0.2534 | 0.2467 | 0.2436 | 0.2405 | 0.2345
| 14 | 0.223 | 0.2166 | 0.2107 | 0.205 | 0.1997 | 0.1947 | 0.1923 | 0.19 | 0.1855
| 15 | 0.1795 | 0.1745 | 0.1699 | 0.1655 | 0.1614 | 0.1574 | 0.1556 | 0.1537 | 0.1502
| 16 | 0.1473 | 0.1434 | 0.1397 | 0.1362 | 0.1329 | 0.1297 | 0.1282 | 0.1267 | 0.1239
| 17 | 0.1229 | 0.1197 | 0.1167 | 0.1138 | 0.1111 | 0.1086 | 0.1073 | 0.1061 | 0.1038
| 18 | 0.1039 | 0.1013 | 0.0988 | 0.0964 | 0.0941 | 0.092 | 0.091 | 0.09 | 0.0881
| 19 | 0.0888 | 0.0866 | 0.0845 | 0.0825 | 0.0806 | 0.0788 | 0.078 | 0.0771 | 0.0755
| 20 | 0.0765 | 0.0746 | 0.0729 | 0.0712 | 0.0696 | 0.0681 | 0.0673 | 0.0666 | 0.0653
| 21 | 0.0655 | 0.0639 | 0.0625 | 0.061 | 0.0597 | 0.0584 | 0.0578 | 0.0572 | 0.0561
| 22 | 0.0558 | 0.0545 | 0.0532 | 0.0521 | 0.0509 | 0.0499 | 0.0494 | 0.0489 | 0.0479
| 23 | 0.0479 | 0.0468 | 0.0458 | 0.0448 | 0.0438 | 0.0429 | 0.0425 | 0.0421 | 0.0413
| 24 | 0.0417 | 0.0408 | 0.0399 | 0.039 | 0.0382 | 0.0375 | 0.0371 | 0.0367 | 0.036
| 25 | 0.0369 | 0.036 | 0.0353 | 0.0345 | 0.0338 | 0.0332 | 0.0328 | 0.0325 | 0.0319
| 26 | 0.0331 | 0.0323 | 0.0316 | 0.031 | 0.0304 | 0.0298 | 0.0295 | 0.0292 | 0.0287
| 27 | 0.0299 | 0.0293 | 0.0287 | 0.0281 | 0.0275 | 0.027 | 0.0268 | 0.0265 | 0.026