## Sheet1
PROPERTIES
General
Name | Gamesa SG 4.7-155 -MOD 4,9MW
Manufacturer | Gamesa
Hub Height | 90 | 102.5 | 120.5
Power
Rated Power | 4900
Peak Power | 4900
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 155
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 27
Restart Wind Speed | 24
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -30
Low Temperature Restart | -20
High Temperature Shutdown | 50
High Temperature Restart | 45
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | III
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 37.5
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.94 | 0.97 | 1 | 1.03 | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.24 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 17 | 19 | 21 | 24 | 27 | 30 | 33 | 36 | 39 | 42 | 44 | 45 | 48
| 3.5 | 75 | 80 | 84 | 89 | 94 | 99 | 104 | 109 | 114 | 119 | 122 | 124 | 129
| 4 | 166 | 174 | 182 | 190 | 198 | 206 | 214 | 223 | 231 | 239 | 243 | 247 | 255
| 4.5 | 284 | 296 | 308 | 320 | 332 | 345 | 357 | 369 | 381 | 393 | 399 | 405 | 417
| 5 | 431 | 448 | 465 | 482 | 499 | 516 | 532 | 549 | 566 | 583 | 592 | 600 | 617
| 5.5 | 609 | 632 | 655 | 678 | 700 | 723 | 745 | 768 | 791 | 813 | 824 | 836 | 858
| 6 | 823 | 853 | 882 | 912 | 941 | 970 | 999 | 1029 | 1058 | 1087 | 1101 | 1116 | 1145
| 6.5 | 1075 | 1113 | 1150 | 1187 | 1224 | 1261 | 1298 | 1335 | 1372 | 1408 | 1427 | 1445 | 1482
| 7 | 1367 | 1414 | 1460 | 1506 | 1552 | 1598 | 1644 | 1690 | 1736 | 1781 | 1804 | 1827 | 1873
| 7.5 | 1701 | 1757 | 1814 | 1871 | 1927 | 1983 | 2040 | 2096 | 2152 | 2208 | 2236 | 2264 | 2320
| 8 | 2075 | 2143 | 2212 | 2280 | 2348 | 2416 | 2484 | 2552 | 2619 | 2687 | 2721 | 2754 | 2821
| 8.5 | 2482 | 2563 | 2644 | 2725 | 2805 | 2886 | 2965 | 3044 | 3123 | 3201 | 3239 | 3277 | 3352
| 9 | 2906 | 3000 | 3094 | 3186 | 3278 | 3368 | 3457 | 3544 | 3628 | 3710 | 3749 | 3789 | 3864
| 9.5 | 3329 | 3434 | 3537 | 3637 | 3735 | 3829 | 3918 | 4004 | 4084 | 4160 | 4196 | 4232 | 4297
| 10 | 3732 | 3842 | 3947 | 4047 | 4140 | 4228 | 4308 | 4382 | 4449 | 4510 | 4538 | 4565 | 4613
| 10.5 | 4095 | 4200 | 4298 | 4387 | 4467 | 4538 | 4600 | 4655 | 4702 | 4742 | 4759 | 4775 | 4801
| 11 | 4399 | 4491 | 4571 | 4641 | 4699 | 4747 | 4786 | 4815 | 4836 | 4852 | 4857 | 4863 | 4871
| 11.5 | 4634 | 4703 | 4759 | 4802 | 4831 | 4851 | 4865 | 4873 | 4879 | 4884 | 4885 | 4887 | 4890
| 12 | 4790 | 4829 | 4853 | 4868 | 4877 | 4883 | 4887 | 4890 | 4892 | 4893 | 4894 | 4895 | 4896
| 12.5 | 4863 | 4876 | 4883 | 4887 | 4890 | 4893 | 4894 | 4896 | 4897 | 4898 | 4898 | 4898 | 4899
| 13 | 4885 | 4889 | 4892 | 4894 | 4896 | 4897 | 4898 | 4899 | 4899 | 4900 | 4900 | 4900 | 4900
| 13.5 | 4893 | 4895 | 4897 | 4898 | 4899 | 4899 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900
| 14 | 4897 | 4898 | 4899 | 4899 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900
| 14.5 | 4899 | 4899 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900
| 15 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900
| 15.5 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900
| 16 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900
| 16.5 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900 | 4900
| 17 | 4899 | 4899 | 4899 | 4899 | 4899 | 4899 | 4899 | 4899 | 4899 | 4899 | 4899 | 4899 | 4899
| 17.5 | 4897 | 4897 | 4897 | 4897 | 4897 | 4897 | 4897 | 4897 | 4897 | 4897 | 4897 | 4897 | 4897
| 18 | 4894 | 4894 | 4894 | 4894 | 4894 | 4894 | 4894 | 4894 | 4894 | 4894 | 4894 | 4894 | 4894
| 18.5 | 4888 | 4888 | 4888 | 4888 | 4888 | 4888 | 4888 | 4888 | 4888 | 4888 | 4888 | 4888 | 4888
| 19 | 4879 | 4879 | 4879 | 4879 | 4879 | 4879 | 4879 | 4879 | 4879 | 4879 | 4879 | 4879 | 4879
| 19.5 | 4864 | 4864 | 4864 | 4864 | 4864 | 4864 | 4864 | 4864 | 4864 | 4864 | 4864 | 4864 | 4864
| 20 | 4835 | 4835 | 4835 | 4835 | 4835 | 4835 | 4835 | 4835 | 4835 | 4835 | 4835 | 4835 | 4835
| 20.5 | 4772 | 4772 | 4772 | 4772 | 4772 | 4772 | 4772 | 4772 | 4772 | 4772 | 4772 | 4772 | 4772
| 21 | 4679 | 4679 | 4679 | 4679 | 4679 | 4679 | 4679 | 4679 | 4679 | 4679 | 4679 | 4679 | 4679
| 21.5 | 4576 | 4576 | 4576 | 4576 | 4576 | 4576 | 4576 | 4576 | 4576 | 4576 | 4576 | 4576 | 4576
| 22 | 4470 | 4470 | 4470 | 4470 | 4470 | 4470 | 4470 | 4470 | 4470 | 4470 | 4470 | 4470 | 4470
| 22.5 | 4368 | 4368 | 4368 | 4368 | 4368 | 4368 | 4368 | 4368 | 4368 | 4368 | 4368 | 4368 | 4368
| 23 | 4271 | 4271 | 4271 | 4271 | 4271 | 4271 | 4271 | 4271 | 4271 | 4271 | 4271 | 4271 | 4271
| 23.5 | 4184 | 4184 | 4184 | 4184 | 4184 | 4184 | 4184 | 4184 | 4184 | 4184 | 4184 | 4184 | 4184
| 24 | 4106 | 4106 | 4106 | 4106 | 4106 | 4106 | 4106 | 4106 | 4106 | 4106 | 4106 | 4106 | 4106
| 24.5 | 4039 | 4039 | 4039 | 4039 | 4039 | 4039 | 4039 | 4039 | 4039 | 4039 | 4039 | 4039 | 4039
| 25 | 3983 | 3983 | 3983 | 3983 | 3983 | 3983 | 3983 | 3983 | 3983 | 3983 | 3983 | 3983 | 3983
| 25.5 | 3937 | 3937 | 3937 | 3937 | 3937 | 3937 | 3937 | 3937 | 3937 | 3937 | 3937 | 3937 | 3937
| 26 | 3896 | 3896 | 3896 | 3896 | 3896 | 3896 | 3896 | 3896 | 3896 | 3896 | 3896 | 3896 | 3896
| 26.5 | 3863 | 3863 | 3863 | 3863 | 3863 | 3863 | 3863 | 3863 | 3863 | 3863 | 3863 | 3863 | 3863
| 27 | 3832 | 3832 | 3832 | 3832 | 3832 | 3832 | 3832 | 3832 | 3832 | 3832 | 3832 | 3832 | 3832

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.94 | 0.97 | 1 | 1.03 | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.24 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115
| 3.5 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532
| 4 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8335
| 4.5 | 0.8196 | 0.8197 | 0.8198 | 0.8198 | 0.8199 | 0.82 | 0.82 | 0.8201 | 0.8201 | 0.8202 | 0.8202 | 0.8202 | 0.8202
| 5 | 0.8072 | 0.8077 | 0.8081 | 0.8084 | 0.8087 | 0.809 | 0.8093 | 0.8095 | 0.8097 | 0.8098 | 0.8098 | 0.8099 | 0.81
| 5.5 | 0.8014 | 0.8021 | 0.8027 | 0.8031 | 0.8035 | 0.8039 | 0.8043 | 0.8046 | 0.8048 | 0.805 | 0.805 | 0.8051 | 0.8053
| 6 | 0.8018 | 0.8023 | 0.8028 | 0.8031 | 0.8034 | 0.8037 | 0.804 | 0.8042 | 0.8044 | 0.8046 | 0.8047 | 0.8047 | 0.8049
| 6.5 | 0.8038 | 0.8041 | 0.8044 | 0.8046 | 0.8048 | 0.805 | 0.8051 | 0.8053 | 0.8054 | 0.8055 | 0.8055 | 0.8056 | 0.8057
| 7 | 0.8052 | 0.8054 | 0.8055 | 0.8057 | 0.8058 | 0.8059 | 0.806 | 0.8061 | 0.8062 | 0.8062 | 0.8063 | 0.8063 | 0.8064
| 7.5 | 0.8049 | 0.805 | 0.8051 | 0.8052 | 0.8052 | 0.8053 | 0.8054 | 0.8054 | 0.8054 | 0.8055 | 0.8055 | 0.8055 | 0.8055
| 8 | 0.799 | 0.7991 | 0.7991 | 0.7992 | 0.7992 | 0.7992 | 0.7992 | 0.7992 | 0.7992 | 0.7991 | 0.799 | 0.7989 | 0.7987
| 8.5 | 0.7816 | 0.7816 | 0.7816 | 0.7816 | 0.7816 | 0.7814 | 0.7812 | 0.7809 | 0.7804 | 0.7797 | 0.7792 | 0.7788 | 0.7775
| 9 | 0.7497 | 0.7497 | 0.7495 | 0.7492 | 0.7487 | 0.748 | 0.747 | 0.7456 | 0.7436 | 0.7412 | 0.7397 | 0.7382 | 0.7346
| 9.5 | 0.7061 | 0.7056 | 0.7049 | 0.7037 | 0.702 | 0.6996 | 0.6967 | 0.6929 | 0.6884 | 0.6832 | 0.6803 | 0.6773 | 0.6705
| 10 | 0.6557 | 0.6541 | 0.6518 | 0.6487 | 0.6447 | 0.6399 | 0.6341 | 0.6275 | 0.62 | 0.6117 | 0.6073 | 0.6029 | 0.5934
| 10.5 | 0.6021 | 0.5985 | 0.5938 | 0.5881 | 0.5814 | 0.5737 | 0.5651 | 0.5558 | 0.5457 | 0.5353 | 0.5298 | 0.5244 | 0.513
| 11 | 0.5471 | 0.5409 | 0.5336 | 0.5252 | 0.5159 | 0.5058 | 0.495 | 0.4836 | 0.4718 | 0.4599 | 0.454 | 0.4482 | 0.4366
| 11.5 | 0.492 | 0.4834 | 0.4736 | 0.463 | 0.4514 | 0.4395 | 0.4275 | 0.4156 | 0.4041 | 0.393 | 0.3877 | 0.3824 | 0.3723
| 12 | 0.438 | 0.427 | 0.4152 | 0.4032 | 0.3912 | 0.3796 | 0.3685 | 0.3579 | 0.3478 | 0.3383 | 0.3337 | 0.3292 | 0.3206
| 12.5 | 0.3857 | 0.3737 | 0.3619 | 0.3506 | 0.3398 | 0.3296 | 0.32 | 0.3108 | 0.3022 | 0.294 | 0.2901 | 0.2863 | 0.279
| 13 | 0.3385 | 0.3273 | 0.3168 | 0.3068 | 0.2974 | 0.2886 | 0.2802 | 0.2724 | 0.265 | 0.258 | 0.2546 | 0.2514 | 0.2451
| 13.5 | 0.2983 | 0.2885 | 0.2792 | 0.2705 | 0.2623 | 0.2547 | 0.2474 | 0.2406 | 0.2342 | 0.2282 | 0.2253 | 0.2224 | 0.217
| 14 | 0.2646 | 0.2559 | 0.2478 | 0.2402 | 0.233 | 0.2263 | 0.22 | 0.2141 | 0.2085 | 0.2032 | 0.2007 | 0.1982 | 0.1935
| 14.5 | 0.236 | 0.2284 | 0.2212 | 0.2146 | 0.2083 | 0.2024 | 0.1969 | 0.1917 | 0.1867 | 0.1821 | 0.1799 | 0.1777 | 0.1735
| 15 | 0.2118 | 0.205 | 0.1987 | 0.1928 | 0.1872 | 0.182 | 0.1771 | 0.1725 | 0.1682 | 0.1641 | 0.1621 | 0.1602 | 0.1565
| 15.5 | 0.191 | 0.185 | 0.1793 | 0.1741 | 0.1692 | 0.1645 | 0.1602 | 0.1561 | 0.1522 | 0.1485 | 0.1468 | 0.145 | 0.1417
| 16 | 0.173 | 0.1676 | 0.1626 | 0.1579 | 0.1535 | 0.1494 | 0.1455 | 0.1418 | 0.1383 | 0.135 | 0.1335 | 0.1319 | 0.129
| 16.5 | 0.1574 | 0.1526 | 0.1481 | 0.1439 | 0.1399 | 0.1362 | 0.1327 | 0.1294 | 0.1262 | 0.1232 | 0.1218 | 0.1204 | 0.1178
| 17 | 0.1438 | 0.1394 | 0.1353 | 0.1315 | 0.128 | 0.1246 | 0.1214 | 0.1184 | 0.1156 | 0.1129 | 0.1116 | 0.1103 | 0.1079
| 17.5 | 0.1317 | 0.1278 | 0.1241 | 0.1207 | 0.1174 | 0.1144 | 0.1115 | 0.1088 | 0.1062 | 0.1037 | 0.1026 | 0.1014 | 0.0992
| 18 | 0.1211 | 0.1175 | 0.1142 | 0.111 | 0.1081 | 0.1053 | 0.1027 | 0.1002 | 0.0978 | 0.0956 | 0.0945 | 0.0935 | 0.0915
| 18.5 | 0.1117 | 0.1084 | 0.1053 | 0.1024 | 0.0997 | 0.0972 | 0.0948 | 0.0925 | 0.0904 | 0.0883 | 0.0874 | 0.0864 | 0.0846
| 19 | 0.1032 | 0.1002 | 0.0974 | 0.0948 | 0.0923 | 0.0899 | 0.0877 | 0.0857 | 0.0837 | 0.0818 | 0.0809 | 0.0801 | 0.0784
| 19.5 | 0.0955 | 0.0928 | 0.0902 | 0.0878 | 0.0855 | 0.0834 | 0.0814 | 0.0795 | 0.0776 | 0.0759 | 0.0751 | 0.0743 | 0.0728
| 20 | 0.0885 | 0.0859 | 0.0836 | 0.0814 | 0.0793 | 0.0773 | 0.0754 | 0.0737 | 0.072 | 0.0705 | 0.0697 | 0.069 | 0.0675
| 20.5 | 0.0816 | 0.0793 | 0.0771 | 0.0751 | 0.0732 | 0.0714 | 0.0697 | 0.0681 | 0.0666 | 0.0651 | 0.0644 | 0.0638 | 0.0624
| 21 | 0.0749 | 0.0728 | 0.0709 | 0.069 | 0.0673 | 0.0657 | 0.0641 | 0.0627 | 0.0613 | 0.06 | 0.0593 | 0.0587 | 0.0575
| 21.5 | 0.0688 | 0.0669 | 0.0651 | 0.0634 | 0.0619 | 0.0604 | 0.059 | 0.0577 | 0.0564 | 0.0552 | 0.0546 | 0.0541 | 0.053
| 22 | 0.0632 | 0.0615 | 0.0599 | 0.0584 | 0.0569 | 0.0556 | 0.0543 | 0.0531 | 0.052 | 0.0509 | 0.0504 | 0.0498 | 0.0489
| 22.5 | 0.0583 | 0.0567 | 0.0552 | 0.0538 | 0.0525 | 0.0513 | 0.0501 | 0.049 | 0.048 | 0.047 | 0.0465 | 0.0461 | 0.0452
| 23 | 0.0539 | 0.0524 | 0.0511 | 0.0498 | 0.0486 | 0.0475 | 0.0464 | 0.0454 | 0.0445 | 0.0436 | 0.0431 | 0.0427 | 0.0419
| 23.5 | 0.05 | 0.0487 | 0.0474 | 0.0463 | 0.0452 | 0.0441 | 0.0431 | 0.0422 | 0.0413 | 0.0405 | 0.0401 | 0.0397 | 0.039
| 24 | 0.0466 | 0.0454 | 0.0442 | 0.0431 | 0.0421 | 0.0412 | 0.0402 | 0.0394 | 0.0386 | 0.0378 | 0.0374 | 0.0371 | 0.0364
| 24.5 | 0.0436 | 0.0425 | 0.0414 | 0.0404 | 0.0394 | 0.0386 | 0.0377 | 0.0369 | 0.0362 | 0.0355 | 0.0351 | 0.0348 | 0.0341
| 25 | 0.041 | 0.0399 | 0.0389 | 0.038 | 0.0371 | 0.0363 | 0.0355 | 0.0347 | 0.034 | 0.0334 | 0.0331 | 0.0327 | 0.0321
| 25.5 | 0.0387 | 0.0377 | 0.0368 | 0.0359 | 0.035 | 0.0343 | 0.0335 | 0.0328 | 0.0322 | 0.0316 | 0.0313 | 0.031 | 0.0304
| 26 | 0.0366 | 0.0357 | 0.0348 | 0.034 | 0.0332 | 0.0325 | 0.0318 | 0.0311 | 0.0305 | 0.0299 | 0.0296 | 0.0293 | 0.0288
| 26.5 | 0.0348 | 0.0339 | 0.0331 | 0.0323 | 0.0316 | 0.0309 | 0.0302 | 0.0296 | 0.029 | 0.0284 | 0.0282 | 0.0279 | 0.0274
| 27 | 0.0331 | 0.0323 | 0.0315 | 0.0307 | 0.03 | 0.0294 | 0.0288 | 0.0282 | 0.0276 | 0.0271 | 0.0268 | 0.0266 | 0.0261