## Sheet1
PROPERTIES
General
Name | Gamesa SG 4.7-155 -MOD 5 MW
Manufacturer | Gamesa
Hub Height | 90 | 102.5 | 120.5
Power
Rated Power | 5000
Peak Power | 5000
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 155
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 27
Restart Wind Speed | 24
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -30
Low Temperature Restart | -20
High Temperature Shutdown | 50
High Temperature Restart | 45
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | III
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 37.5
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.94 | 0.97 | 1 | 1.03 | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.24 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 17 | 19 | 21 | 24 | 27 | 30 | 33 | 36 | 39 | 42 | 44 | 45 | 48
| 3.5 | 75 | 80 | 84 | 89 | 94 | 99 | 104 | 109 | 114 | 119 | 122 | 124 | 129
| 4 | 166 | 174 | 182 | 190 | 198 | 206 | 214 | 223 | 231 | 239 | 243 | 247 | 255
| 4.5 | 284 | 296 | 308 | 320 | 332 | 345 | 357 | 369 | 381 | 393 | 399 | 405 | 417
| 5 | 431 | 448 | 465 | 482 | 499 | 516 | 532 | 549 | 566 | 583 | 592 | 600 | 617
| 5.5 | 609 | 632 | 655 | 678 | 700 | 723 | 745 | 768 | 791 | 813 | 824 | 836 | 858
| 6 | 823 | 853 | 882 | 912 | 941 | 970 | 999 | 1029 | 1058 | 1087 | 1101 | 1116 | 1145
| 6.5 | 1075 | 1113 | 1150 | 1187 | 1224 | 1261 | 1298 | 1335 | 1372 | 1408 | 1427 | 1445 | 1482
| 7 | 1367 | 1414 | 1460 | 1506 | 1552 | 1598 | 1644 | 1690 | 1736 | 1781 | 1804 | 1827 | 1873
| 7.5 | 1701 | 1757 | 1814 | 1871 | 1927 | 1983 | 2040 | 2096 | 2152 | 2208 | 2236 | 2264 | 2320
| 8 | 2075 | 2143 | 2212 | 2280 | 2348 | 2416 | 2484 | 2552 | 2620 | 2687 | 2721 | 2755 | 2822
| 8.5 | 2482 | 2563 | 2644 | 2725 | 2806 | 2886 | 2966 | 3046 | 3125 | 3203 | 3242 | 3280 | 3356
| 9 | 2907 | 3001 | 3094 | 3187 | 3279 | 3371 | 3461 | 3549 | 3635 | 3719 | 3759 | 3800 | 3878
| 9.5 | 3330 | 3436 | 3540 | 3642 | 3741 | 3838 | 3930 | 4019 | 4103 | 4183 | 4221 | 4258 | 4328
| 10 | 3736 | 3848 | 3956 | 4060 | 4158 | 4249 | 4335 | 4414 | 4486 | 4552 | 4582 | 4611 | 4664
| 10.5 | 4106 | 4217 | 4319 | 4414 | 4500 | 4577 | 4646 | 4707 | 4759 | 4805 | 4825 | 4843 | 4875
| 11 | 4424 | 4523 | 4610 | 4687 | 4752 | 4808 | 4853 | 4890 | 4917 | 4938 | 4945 | 4952 | 4963
| 11.5 | 4675 | 4753 | 4818 | 4869 | 4909 | 4935 | 4953 | 4966 | 4974 | 4980 | 4982 | 4984 | 4987
| 12 | 4853 | 4903 | 4936 | 4957 | 4970 | 4978 | 4983 | 4987 | 4990 | 4992 | 4993 | 4994 | 4995
| 12.5 | 4948 | 4967 | 4978 | 4984 | 4988 | 4991 | 4993 | 4995 | 4996 | 4997 | 4997 | 4998 | 4998
| 13 | 4981 | 4987 | 4990 | 4993 | 4995 | 4996 | 4997 | 4998 | 4999 | 4999 | 4999 | 5000 | 5000
| 13.5 | 4991 | 4994 | 4996 | 4997 | 4998 | 4999 | 4999 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
| 14 | 4996 | 4997 | 4998 | 4999 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
| 14.5 | 4998 | 4999 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
| 15 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
| 15.5 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
| 16 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
| 16.5 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 4999
| 17 | 4999 | 4999 | 4999 | 4999 | 4999 | 4999 | 4999 | 4999 | 4999 | 4999 | 4999 | 4999 | 4999
| 17.5 | 4997 | 4997 | 4997 | 4997 | 4997 | 4997 | 4997 | 4997 | 4997 | 4997 | 4997 | 4997 | 4997
| 18 | 4993 | 4993 | 4993 | 4993 | 4993 | 4993 | 4993 | 4993 | 4993 | 4993 | 4993 | 4993 | 4993
| 18.5 | 4987 | 4987 | 4987 | 4987 | 4987 | 4987 | 4987 | 4987 | 4987 | 4987 | 4987 | 4987 | 4987
| 19 | 4977 | 4977 | 4977 | 4977 | 4977 | 4977 | 4977 | 4977 | 4977 | 4977 | 4977 | 4977 | 4977
| 19.5 | 4959 | 4959 | 4959 | 4959 | 4959 | 4959 | 4959 | 4959 | 4959 | 4959 | 4959 | 4959 | 4959
| 20 | 4922 | 4922 | 4922 | 4922 | 4922 | 4922 | 4922 | 4922 | 4922 | 4922 | 4922 | 4922 | 4922
| 20.5 | 4847 | 4847 | 4847 | 4847 | 4847 | 4847 | 4847 | 4847 | 4847 | 4847 | 4847 | 4847 | 4847
| 21 | 4745 | 4745 | 4745 | 4745 | 4745 | 4745 | 4745 | 4745 | 4745 | 4745 | 4745 | 4745 | 4745
| 21.5 | 4633 | 4633 | 4633 | 4633 | 4633 | 4633 | 4633 | 4633 | 4633 | 4633 | 4633 | 4633 | 4633
| 22 | 4518 | 4518 | 4518 | 4518 | 4518 | 4518 | 4518 | 4518 | 4518 | 4518 | 4518 | 4518 | 4518
| 22.5 | 4407 | 4407 | 4407 | 4407 | 4407 | 4407 | 4407 | 4407 | 4407 | 4407 | 4407 | 4407 | 4407
| 23 | 4303 | 4303 | 4303 | 4303 | 4303 | 4303 | 4303 | 4303 | 4303 | 4303 | 4303 | 4303 | 4303
| 23.5 | 4210 | 4210 | 4210 | 4210 | 4210 | 4210 | 4210 | 4210 | 4210 | 4210 | 4210 | 4210 | 4210
| 24 | 4127 | 4127 | 4127 | 4127 | 4127 | 4127 | 4127 | 4127 | 4127 | 4127 | 4127 | 4127 | 4127
| 24.5 | 4056 | 4056 | 4056 | 4056 | 4056 | 4056 | 4056 | 4056 | 4056 | 4056 | 4056 | 4056 | 4056
| 25 | 3996 | 3996 | 3996 | 3996 | 3996 | 3996 | 3996 | 3996 | 3996 | 3996 | 3996 | 3996 | 3996
| 25.5 | 3947 | 3947 | 3947 | 3947 | 3947 | 3947 | 3947 | 3947 | 3947 | 3947 | 3947 | 3947 | 3947
| 26 | 3904 | 3904 | 3904 | 3904 | 3904 | 3904 | 3904 | 3904 | 3904 | 3904 | 3904 | 3904 | 3904
| 26.5 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870
| 27 | 3838 | 3838 | 3838 | 3838 | 3838 | 3838 | 3838 | 3838 | 3838 | 3838 | 3838 | 3838 | 3838

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.94 | 0.97 | 1 | 1.03 | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.24 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115 | 0.9115
| 3.5 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532 | 0.8532
| 4 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8334 | 0.8335
| 4.5 | 0.8196 | 0.8197 | 0.8198 | 0.8198 | 0.8199 | 0.82 | 0.82 | 0.8201 | 0.8201 | 0.8202 | 0.8202 | 0.8202 | 0.8202
| 5 | 0.8072 | 0.8077 | 0.8081 | 0.8084 | 0.8087 | 0.809 | 0.8093 | 0.8095 | 0.8097 | 0.8098 | 0.8098 | 0.8099 | 0.81
| 5.5 | 0.8014 | 0.8021 | 0.8027 | 0.8031 | 0.8035 | 0.8039 | 0.8043 | 0.8046 | 0.8048 | 0.805 | 0.805 | 0.8051 | 0.8053
| 6 | 0.8018 | 0.8023 | 0.8028 | 0.8031 | 0.8034 | 0.8037 | 0.804 | 0.8042 | 0.8044 | 0.8046 | 0.8047 | 0.8047 | 0.8049
| 6.5 | 0.8038 | 0.8041 | 0.8044 | 0.8046 | 0.8048 | 0.805 | 0.8051 | 0.8053 | 0.8054 | 0.8055 | 0.8055 | 0.8056 | 0.8057
| 7 | 0.8052 | 0.8054 | 0.8055 | 0.8057 | 0.8058 | 0.8059 | 0.806 | 0.8061 | 0.8062 | 0.8062 | 0.8063 | 0.8063 | 0.8064
| 7.5 | 0.8049 | 0.805 | 0.8051 | 0.8052 | 0.8052 | 0.8053 | 0.8054 | 0.8054 | 0.8055 | 0.8055 | 0.8055 | 0.8055 | 0.8055
| 8 | 0.799 | 0.7991 | 0.7991 | 0.7992 | 0.7992 | 0.7992 | 0.7993 | 0.7993 | 0.7992 | 0.7992 | 0.7991 | 0.7991 | 0.7989
| 8.5 | 0.7816 | 0.7816 | 0.7816 | 0.7816 | 0.7816 | 0.7816 | 0.7814 | 0.7812 | 0.7808 | 0.7803 | 0.78 | 0.7796 | 0.7786
| 9 | 0.7498 | 0.7497 | 0.7496 | 0.7494 | 0.7491 | 0.7486 | 0.7478 | 0.7467 | 0.7452 | 0.7432 | 0.742 | 0.7407 | 0.7376
| 9.5 | 0.7063 | 0.706 | 0.7054 | 0.7045 | 0.7032 | 0.7014 | 0.6989 | 0.6959 | 0.692 | 0.6874 | 0.6848 | 0.6822 | 0.6762
| 10 | 0.6564 | 0.6552 | 0.6534 | 0.6509 | 0.6476 | 0.6435 | 0.6384 | 0.6326 | 0.6259 | 0.6184 | 0.6143 | 0.6102 | 0.6013
| 10.5 | 0.6038 | 0.6009 | 0.597 | 0.5921 | 0.5862 | 0.5794 | 0.5715 | 0.5629 | 0.5536 | 0.5437 | 0.5386 | 0.5334 | 0.5226
| 11 | 0.5502 | 0.545 | 0.5386 | 0.531 | 0.5225 | 0.5133 | 0.5031 | 0.4924 | 0.4811 | 0.4695 | 0.4637 | 0.4579 | 0.4465
| 11.5 | 0.4967 | 0.4891 | 0.4802 | 0.4703 | 0.4597 | 0.4482 | 0.4365 | 0.4248 | 0.4132 | 0.402 | 0.3966 | 0.3913 | 0.3809
| 12 | 0.4442 | 0.4343 | 0.4231 | 0.4115 | 0.3997 | 0.3881 | 0.3768 | 0.3661 | 0.3558 | 0.346 | 0.3413 | 0.3368 | 0.3279
| 12.5 | 0.3932 | 0.3815 | 0.3698 | 0.3584 | 0.3475 | 0.3371 | 0.3272 | 0.3179 | 0.309 | 0.3007 | 0.2966 | 0.2928 | 0.2853
| 13 | 0.3458 | 0.3346 | 0.3238 | 0.3137 | 0.3041 | 0.295 | 0.2865 | 0.2784 | 0.2708 | 0.2637 | 0.2602 | 0.2569 | 0.2505
| 13.5 | 0.3049 | 0.2948 | 0.2854 | 0.2765 | 0.2681 | 0.2602 | 0.2528 | 0.2459 | 0.2393 | 0.2331 | 0.2301 | 0.2272 | 0.2216
| 14 | 0.2704 | 0.2615 | 0.2532 | 0.2454 | 0.2381 | 0.2312 | 0.2247 | 0.2186 | 0.2129 | 0.2075 | 0.2049 | 0.2024 | 0.1975
| 14.5 | 0.2411 | 0.2333 | 0.226 | 0.2191 | 0.2127 | 0.2067 | 0.201 | 0.1957 | 0.1906 | 0.1859 | 0.1836 | 0.1814 | 0.1771
| 15 | 0.2163 | 0.2094 | 0.2029 | 0.1968 | 0.1912 | 0.1858 | 0.1808 | 0.1761 | 0.1716 | 0.1674 | 0.1654 | 0.1634 | 0.1596
| 15.5 | 0.195 | 0.1888 | 0.1831 | 0.1777 | 0.1727 | 0.1679 | 0.1634 | 0.1592 | 0.1553 | 0.1515 | 0.1497 | 0.1479 | 0.1446
| 16 | 0.1766 | 0.1711 | 0.166 | 0.1612 | 0.1566 | 0.1524 | 0.1484 | 0.1446 | 0.1411 | 0.1377 | 0.1361 | 0.1345 | 0.1315
| 16.5 | 0.1606 | 0.1557 | 0.1511 | 0.1468 | 0.1427 | 0.1389 | 0.1353 | 0.1319 | 0.1287 | 0.1257 | 0.1242 | 0.1228 | 0.12
| 17 | 0.1467 | 0.1422 | 0.1381 | 0.1342 | 0.1305 | 0.127 | 0.1238 | 0.1207 | 0.1178 | 0.1151 | 0.1138 | 0.1125 | 0.11
| 17.5 | 0.1344 | 0.1303 | 0.1266 | 0.123 | 0.1197 | 0.1166 | 0.1136 | 0.1108 | 0.1082 | 0.1057 | 0.1045 | 0.1033 | 0.1011
| 18 | 0.1235 | 0.1198 | 0.1164 | 0.1132 | 0.1102 | 0.1073 | 0.1046 | 0.1021 | 0.0997 | 0.0974 | 0.0963 | 0.0953 | 0.0932
| 18.5 | 0.1138 | 0.1105 | 0.1074 | 0.1044 | 0.1017 | 0.099 | 0.0966 | 0.0943 | 0.0921 | 0.09 | 0.089 | 0.088 | 0.0861
| 19 | 0.1052 | 0.1021 | 0.0992 | 0.0966 | 0.094 | 0.0916 | 0.0894 | 0.0873 | 0.0852 | 0.0833 | 0.0824 | 0.0815 | 0.0798
| 19.5 | 0.0973 | 0.0945 | 0.0919 | 0.0894 | 0.0871 | 0.0849 | 0.0829 | 0.0809 | 0.0791 | 0.0773 | 0.0765 | 0.0756 | 0.0741
| 20 | 0.09 | 0.0874 | 0.085 | 0.0828 | 0.0806 | 0.0786 | 0.0767 | 0.0749 | 0.0732 | 0.0716 | 0.0709 | 0.0701 | 0.0686
| 20.5 | 0.0828 | 0.0805 | 0.0783 | 0.0762 | 0.0743 | 0.0724 | 0.0707 | 0.0691 | 0.0675 | 0.0661 | 0.0654 | 0.0647 | 0.0633
| 21 | 0.0759 | 0.0738 | 0.0718 | 0.0699 | 0.0682 | 0.0665 | 0.065 | 0.0635 | 0.0621 | 0.0607 | 0.0601 | 0.0595 | 0.0583
| 21.5 | 0.0696 | 0.0677 | 0.0659 | 0.0642 | 0.0626 | 0.0611 | 0.0597 | 0.0583 | 0.057 | 0.0558 | 0.0552 | 0.0547 | 0.0536
| 22 | 0.0639 | 0.0622 | 0.0605 | 0.059 | 0.0575 | 0.0561 | 0.0549 | 0.0536 | 0.0525 | 0.0514 | 0.0508 | 0.0503 | 0.0493
| 22.5 | 0.0588 | 0.0572 | 0.0557 | 0.0543 | 0.053 | 0.0517 | 0.0506 | 0.0495 | 0.0484 | 0.0474 | 0.0469 | 0.0464 | 0.0455
| 23 | 0.0543 | 0.0528 | 0.0515 | 0.0502 | 0.049 | 0.0478 | 0.0468 | 0.0457 | 0.0448 | 0.0439 | 0.0434 | 0.043 | 0.0422
| 23.5 | 0.0503 | 0.049 | 0.0477 | 0.0465 | 0.0454 | 0.0444 | 0.0434 | 0.0425 | 0.0416 | 0.0407 | 0.0403 | 0.0399 | 0.0392
| 24 | 0.0468 | 0.0456 | 0.0444 | 0.0433 | 0.0423 | 0.0414 | 0.0404 | 0.0396 | 0.0388 | 0.038 | 0.0376 | 0.0373 | 0.0366
| 24.5 | 0.0438 | 0.0426 | 0.0416 | 0.0406 | 0.0396 | 0.0387 | 0.0379 | 0.0371 | 0.0363 | 0.0356 | 0.0352 | 0.0349 | 0.0343
| 25 | 0.0411 | 0.0401 | 0.0391 | 0.0381 | 0.0372 | 0.0364 | 0.0356 | 0.0349 | 0.0342 | 0.0335 | 0.0332 | 0.0328 | 0.0322
| 25.5 | 0.0388 | 0.0378 | 0.0369 | 0.036 | 0.0351 | 0.0344 | 0.0336 | 0.0329 | 0.0323 | 0.0316 | 0.0313 | 0.031 | 0.0305
| 26 | 0.0367 | 0.0358 | 0.0349 | 0.0341 | 0.0333 | 0.0325 | 0.0318 | 0.0312 | 0.0306 | 0.03 | 0.0297 | 0.0294 | 0.0289
| 26.5 | 0.0349 | 0.034 | 0.0331 | 0.0324 | 0.0316 | 0.0309 | 0.0303 | 0.0296 | 0.029 | 0.0285 | 0.0282 | 0.028 | 0.0275
| 27 | 0.0332 | 0.0323 | 0.0315 | 0.0308 | 0.0301 | 0.0294 | 0.0288 | 0.0282 | 0.0277 | 0.0271 | 0.0269 | 0.0266 | 0.0261