## Sheet1
PROPERTIES
General
Name | Gamesa SG 5.0-145 -MOD 4,0 MW
Manufacturer | Gamesa
Hub Height | 91 | 95.5 | 97.5 | 127.5
Power
Rated Power | 4000
Peak Power | 4000
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 145
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 27
Restart Wind Speed | 24
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -30
Low Temperature Restart | -20
High Temperature Shutdown | 45
High Temperature Restart | 45
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | II
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 8.5
Vref | 42.5
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 31 | 33.5 | 36 | 37.6667 | 40 | 42.5 | 44.6667 | 46.5 | 49 | 51.5 | 53.3333 | 56 | 58 | 61.0039
| 3.5 | 87.3333 | 90.8333 | 95 | 99.1667 | 102.6667 | 106.5 | 110.3333 | 113.8333 | 118 | 122.1667 | 125.6667 | 130 | 133.6667 | 138.0167
| 4 | 172.6667 | 179.1667 | 185 | 190.8333 | 197.3333 | 203.5 | 209.6667 | 216.1667 | 222 | 228.6667 | 234.6667 | 241 | 247.3333 | 253.0074
| 4.5 | 281.6667 | 290.8333 | 300 | 309.1667 | 318.3333 | 327.5 | 336.6667 | 345.8333 | 355 | 364.1667 | 373.3333 | 383 | 391.6667 | 400.004
| 5 | 415 | 427.6667 | 441 | 453.5 | 466 | 478.5 | 491.3333 | 504.5 | 517 | 529.5 | 542 | 555 | 568 | 579.0025
| 5.5 | 576 | 593.3333 | 610 | 626.6667 | 644 | 661 | 677.6667 | 694.3333 | 711 | 728.5 | 745.3333 | 762 | 778.6667 | 793.0017
| 6 | 767.6667 | 789.5 | 812 | 833.6667 | 855.3333 | 877.5 | 899.6667 | 921.3333 | 943 | 964.6667 | 987 | 1009 | 1030.6667 | 1049.0013
| 6.5 | 993.3333 | 1021.5 | 1049 | 1076.5 | 1104.6667 | 1132.5 | 1160.3333 | 1188.5 | 1216 | 1244.3333 | 1272 | 1300 | 1327.3333 | 1351.001
| 7 | 1256 | 1290.8333 | 1325 | 1360 | 1395 | 1430 | 1464.6667 | 1499 | 1534 | 1569 | 1603.3333 | 1638 | 1672.6667 | 1701.0007
| 7.5 | 1557 | 1599.5 | 1642 | 1685.3333 | 1728 | 1770.5 | 1813 | 1855.5 | 1898 | 1941.3333 | 1983.3333 | 2026 | 2068 | 2103.0006
| 8 | 1895.6667 | 1947.3333 | 1999 | 2050.6667 | 2102.3333 | 2153.5 | 2204.6667 | 2256.1667 | 2307 | 2357.8333 | 2408 | 2458 | 2507.6667 | 2548.0005
| 8.5 | 2264.3333 | 2325.1667 | 2386 | 2446 | 2506 | 2566 | 2625.3333 | 2683.5 | 2741 | 2797.6667 | 2853 | 2907 | 2959.6667 | 3002.0004
| 9 | 2646 | 2715.5 | 2783 | 2850.5 | 2916 | 2980 | 3042.3333 | 3102.6667 | 3161 | 3216 | 3269.6667 | 3321 | 3369.6667 | 3408.0003
| 9.5 | 3018.3333 | 3091.1667 | 3162 | 3228.6667 | 3292.6667 | 3353.5 | 3411.3333 | 3466.1667 | 3517 | 3563.6667 | 3607 | 3648 | 3685 | 3714.0003
| 10 | 3355 | 3424 | 3489 | 3547.3333 | 3601.6667 | 3651.5 | 3697 | 3738.5 | 3776 | 3809.3333 | 3838 | 3864 | 3886 | 3903.0003
| 10.5 | 3629.6667 | 3687.3333 | 3739 | 3783.1667 | 3822 | 3855.5 | 3884 | 3907.6667 | 3926 | 3940.1667 | 3951 | 3960 | 3966 | 3971.0003
| 11 | 3829.3333 | 3868.5 | 3901 | 3923.5 | 3941.3333 | 3954.5 | 3964 | 3971 | 3976 | 3979.3333 | 3982 | 3985 | 3986.6667 | 3989.0003
| 11.5 | 3941 | 3957.1667 | 3968 | 3974.6667 | 3979.3333 | 3983 | 3985.6667 | 3987.3333 | 3989 | 3990.6667 | 3991.6667 | 3993 | 3994 | 3995.0003
| 12 | 3978.6667 | 3982.6667 | 3986 | 3988.5 | 3990.3333 | 3992 | 3993.3333 | 3994.1667 | 3995 | 3995.8333 | 3996.6667 | 3997 | 3997.3333 | 3999.0003
| 12.5 | 3989.6667 | 3991.3333 | 3993 | 3994.6667 | 3995.6667 | 3996.5 | 3997 | 3997.1667 | 3998 | 3998 | 3998 | 3999 | 3999 | 4000
| 13 | 3994.6667 | 3996.1667 | 3997 | 3997.8333 | 3998 | 3998 | 3998.3333 | 3999 | 3999 | 3999 | 3999 | 3999 | 3999 | 4000
| 13.5 | 3997.3333 | 3998 | 3998 | 3998.8333 | 3999 | 3999 | 3999 | 3999 | 3999 | 3999.8333 | 4000 | 4000 | 4000 | 4000
| 14 | 3999 | 3999 | 3999 | 3999 | 3999.6667 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000
| 14.5 | 3999 | 3999.1667 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000
| 15 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000
| 15.5 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000
| 16 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000
| 16.5 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000
| 17 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000
| 17.5 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000
| 18 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000
| 18.5 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000
| 19 | 3999 | 3999 | 3999 | 3999 | 3999 | 3999 | 3999 | 3999 | 3999 | 3999 | 3999 | 3999 | 3999 | 3999
| 19.5 | 3998 | 3998 | 3998 | 3998 | 3998 | 3998 | 3998 | 3998 | 3998 | 3998 | 3998 | 3998 | 3998 | 3998
| 20 | 3996 | 3996 | 3996 | 3996 | 3996 | 3996 | 3996 | 3996 | 3996 | 3996 | 3996 | 3996 | 3996 | 3996
| 20.5 | 3991 | 3991 | 3991 | 3991 | 3991 | 3991 | 3991 | 3991 | 3991 | 3991 | 3991 | 3991 | 3991 | 3991
| 21 | 3983 | 3983 | 3983 | 3983 | 3983 | 3983 | 3983 | 3983 | 3983 | 3983 | 3983 | 3983 | 3983 | 3983
| 21.5 | 3972 | 3972 | 3972 | 3972 | 3972 | 3972 | 3972 | 3972 | 3972 | 3972 | 3972 | 3972 | 3972 | 3972
| 22 | 3956 | 3956 | 3956 | 3956 | 3956 | 3956 | 3956 | 3956 | 3956 | 3956 | 3956 | 3956 | 3956 | 3956
| 22.5 | 3936 | 3936 | 3936 | 3936 | 3936 | 3936 | 3936 | 3936 | 3936 | 3936 | 3936 | 3936 | 3936 | 3936

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948
| 3.5 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674
| 4 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438
| 4.5 | 0.82807 | 0.82822 | 0.8283 | 0.82838 | 0.82847 | 0.82855 | 0.82863 | 0.82872 | 0.8288 | 0.8288 | 0.82887 | 0.82887 | 0.82887 | 0.82887
| 5 | 0.81813 | 0.81847 | 0.8188 | 0.81905 | 0.8193 | 0.81955 | 0.81977 | 0.81995 | 0.8202 | 0.82037 | 0.82053 | 0.82053 | 0.82053 | 0.82053
| 5.5 | 0.81553 | 0.81588 | 0.8163 | 0.81655 | 0.81687 | 0.81715 | 0.81737 | 0.81755 | 0.8178 | 0.81797 | 0.81813 | 0.81813 | 0.81813 | 0.81813
| 6 | 0.8166 | 0.81685 | 0.8171 | 0.81735 | 0.81753 | 0.8177 | 0.81787 | 0.81802 | 0.8181 | 0.81827 | 0.81837 | 0.81837 | 0.81837 | 0.81837
| 6.5 | 0.81797 | 0.81813 | 0.8183 | 0.81838 | 0.81847 | 0.8186 | 0.81873 | 0.81882 | 0.8189 | 0.81898 | 0.819 | 0.819 | 0.819 | 0.819
| 7 | 0.81853 | 0.81862 | 0.8187 | 0.81878 | 0.81887 | 0.8189 | 0.81893 | 0.81902 | 0.8191 | 0.8191 | 0.81917 | 0.81917 | 0.81917 | 0.81917
| 7.5 | 0.81643 | 0.81652 | 0.8166 | 0.8166 | 0.81667 | 0.8167 | 0.81673 | 0.8168 | 0.8168 | 0.81672 | 0.8167 | 0.8167 | 0.8167 | 0.8167
| 8 | 0.80723 | 0.8073 | 0.8073 | 0.80722 | 0.8072 | 0.8071 | 0.8069 | 0.80663 | 0.8063 | 0.80588 | 0.80527 | 0.80527 | 0.80527 | 0.80527
| 8.5 | 0.78563 | 0.78545 | 0.7852 | 0.78478 | 0.78423 | 0.78345 | 0.7824 | 0.78108 | 0.7795 | 0.7775 | 0.7751 | 0.7751 | 0.7751 | 0.7751
| 9 | 0.74977 | 0.74885 | 0.7476 | 0.74585 | 0.74377 | 0.74115 | 0.738 | 0.73438 | 0.7303 | 0.72547 | 0.72017 | 0.72017 | 0.72017 | 0.72017
| 9.5 | 0.701 | 0.69833 | 0.695 | 0.69083 | 0.686 | 0.68055 | 0.6745 | 0.66788 | 0.6608 | 0.65305 | 0.6449 | 0.6449 | 0.6449 | 0.6449
| 10 | 0.64213 | 0.63677 | 0.6306 | 0.6236 | 0.616 | 0.6078 | 0.59913 | 0.59015 | 0.5809 | 0.57123 | 0.5615 | 0.5615 | 0.5615 | 0.5615
| 10.5 | 0.57707 | 0.56907 | 0.5604 | 0.55115 | 0.54163 | 0.5318 | 0.52177 | 0.51168 | 0.5016 | 0.49152 | 0.48157 | 0.48157 | 0.48157 | 0.48157
| 11 | 0.51063 | 0.5009 | 0.4909 | 0.48065 | 0.4704 | 0.4602 | 0.4501 | 0.44015 | 0.4304 | 0.4209 | 0.41167 | 0.41167 | 0.41167 | 0.41167
| 11.5 | 0.44757 | 0.43725 | 0.427 | 0.41692 | 0.40703 | 0.39735 | 0.38793 | 0.37883 | 0.37 | 0.36158 | 0.35343 | 0.35343 | 0.35343 | 0.35343
| 12 | 0.3909 | 0.38097 | 0.3713 | 0.36197 | 0.3529 | 0.3442 | 0.33583 | 0.32777 | 0.3201 | 0.31277 | 0.30577 | 0.30577 | 0.30577 | 0.30577
| 12.5 | 0.34193 | 0.33283 | 0.324 | 0.31567 | 0.30767 | 0.30005 | 0.29277 | 0.28577 | 0.2791 | 0.27277 | 0.26677 | 0.26677 | 0.26677 | 0.26677
| 13 | 0.3003 | 0.29215 | 0.2844 | 0.27707 | 0.27007 | 0.2634 | 0.25707 | 0.25105 | 0.2453 | 0.2398 | 0.23463 | 0.23463 | 0.23463 | 0.23463
| 13.5 | 0.26527 | 0.25803 | 0.2512 | 0.24478 | 0.2387 | 0.2329 | 0.2274 | 0.22218 | 0.2171 | 0.21243 | 0.2079 | 0.2079 | 0.2079 | 0.2079
| 14 | 0.23563 | 0.2293 | 0.2233 | 0.21772 | 0.2124 | 0.2073 | 0.20243 | 0.19783 | 0.1935 | 0.18933 | 0.18537 | 0.18537 | 0.18537 | 0.18537
| 14.5 | 0.21057 | 0.20503 | 0.1997 | 0.19478 | 0.19007 | 0.1856 | 0.18133 | 0.17723 | 0.1734 | 0.16973 | 0.1662 | 0.1662 | 0.1662 | 0.1662
| 15 | 0.1892 | 0.18425 | 0.1795 | 0.17517 | 0.17097 | 0.167 | 0.16323 | 0.15962 | 0.1562 | 0.15287 | 0.14973 | 0.14973 | 0.14973 | 0.14973
| 15.5 | 0.17073 | 0.16637 | 0.1622 | 0.15828 | 0.1545 | 0.15095 | 0.1476 | 0.14438 | 0.1413 | 0.13838 | 0.1356 | 0.1356 | 0.1356 | 0.1356
| 16 | 0.1548 | 0.15085 | 0.1471 | 0.1436 | 0.14023 | 0.13705 | 0.13403 | 0.13115 | 0.1284 | 0.12573 | 0.1232 | 0.1232 | 0.1232 | 0.1232
| 16.5 | 0.14093 | 0.13733 | 0.134 | 0.13083 | 0.1278 | 0.1249 | 0.12217 | 0.1196 | 0.1171 | 0.11468 | 0.1124 | 0.1124 | 0.1124 | 0.1124
| 17 | 0.1287 | 0.1255 | 0.1225 | 0.11958 | 0.11687 | 0.11425 | 0.11173 | 0.10935 | 0.1071 | 0.10502 | 0.10293 | 0.10293 | 0.10293 | 0.10293
| 17.5 | 0.118 | 0.11505 | 0.1123 | 0.10972 | 0.1072 | 0.1048 | 0.10253 | 0.1004 | 0.0984 | 0.0964 | 0.094533 | 0.094533 | 0.094533 | 0.094533
| 18 | 0.1085 | 0.1058 | 0.1033 | 0.10088 | 0.0986 | 0.09645 | 0.0944 | 0.092433 | 0.0906 | 0.088767 | 0.087067 | 0.087067 | 0.087067 | 0.087067
| 18.5 | 0.10003 | 0.097633 | 0.0953 | 0.093133 | 0.091033 | 0.08905 | 0.087167 | 0.08535 | 0.0836 | 0.082017 | 0.080433 | 0.080433 | 0.080433 | 0.080433
| 19 | 0.0925 | 0.090267 | 0.0881 | 0.0861 | 0.084233 | 0.0824 | 0.080633 | 0.078983 | 0.0774 | 0.0759 | 0.074467 | 0.074467 | 0.074467 | 0.074467
| 19.5 | 0.085667 | 0.083617 | 0.0817 | 0.079867 | 0.0781 | 0.0764 | 0.0748 | 0.0733 | 0.0718 | 0.070467 | 0.069133 | 0.069133 | 0.069133 | 0.069133
| 20 | 0.079533 | 0.07765 | 0.0759 | 0.07415 | 0.072533 | 0.071 | 0.069533 | 0.068133 | 0.0668 | 0.065467 | 0.064267 | 0.064267 | 0.064267 | 0.064267
| 20.5 | 0.074 | 0.072267 | 0.0706 | 0.069017 | 0.0675 | 0.0661 | 0.064767 | 0.06345 | 0.0622 | 0.061033 | 0.059867 | 0.059867 | 0.059867 | 0.059867
| 21 | 0.068933 | 0.0673 | 0.0658 | 0.0643 | 0.062933 | 0.0616 | 0.060333 | 0.059167 | 0.058 | 0.056917 | 0.055833 | 0.055833 | 0.055833 | 0.055833
| 21.5 | 0.0643 | 0.062817 | 0.0614 | 0.060067 | 0.058733 | 0.0575 | 0.056367 | 0.055283 | 0.0542 | 0.0532 | 0.0522 | 0.0522 | 0.0522 | 0.0522
| 22 | 0.060033 | 0.058633 | 0.0573 | 0.05605 | 0.054867 | 0.05375 | 0.052667 | 0.0516 | 0.0506 | 0.049683 | 0.048767 | 0.048767 | 0.048767 | 0.048767
| 22.5 | 0.056167 | 0.054867 | 0.0537 | 0.052533 | 0.051367 | 0.0503 | 0.0493 | 0.048317 | 0.0474 | 0.046567 | 0.045733 | 0.045733 | 0.045733 | 0.045733