## Sheet1
PROPERTIES
General
Name | Gamesa SG 5.0-145 -MOD 4,5 MW
Manufacturer | Gamesa
Hub Height | 91 | 95.5 | 97.5 | 127.5
Power
Rated Power | 4500
Peak Power | 4500
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 145
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 27
Restart Wind Speed | 24
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -30
Low Temperature Restart | -20
High Temperature Shutdown | 45
High Temperature Restart | 45
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | II
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 8.5
Vref | 42.5
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 31 | 33.5 | 36 | 37.6667 | 40 | 42.5 | 44.6667 | 46.5 | 49 | 51.5 | 53.3333 | 56 | 58 | 61.0039
| 3.5 | 87.3333 | 90.8333 | 95 | 99.1667 | 102.6667 | 106.5 | 110.3333 | 113.8333 | 118 | 122.1667 | 125.6667 | 130 | 133.6667 | 138.0167
| 4 | 172.6667 | 179.1667 | 185 | 190.8333 | 197.3333 | 203.5 | 209.6667 | 216.1667 | 222 | 228.6667 | 234.6667 | 241 | 247.3333 | 253.0074
| 4.5 | 281.6667 | 290.8333 | 300 | 309.1667 | 318.3333 | 327.5 | 336.6667 | 345.8333 | 355 | 364.1667 | 373.3333 | 383 | 391.6667 | 400.004
| 5 | 415 | 427.6667 | 441 | 453.5 | 466 | 478.5 | 491.3333 | 504.5 | 517 | 529.5 | 542 | 555 | 568 | 579.0025
| 5.5 | 576 | 593.3333 | 610 | 626.6667 | 644 | 661 | 677.6667 | 694.3333 | 711 | 728.5 | 745.3333 | 762 | 778.6667 | 793.0017
| 6 | 767.6667 | 789.5 | 812 | 833.6667 | 855.3333 | 877.5 | 899.6667 | 921.3333 | 943 | 964.6667 | 987 | 1009 | 1030.6667 | 1049.0013
| 6.5 | 993.3333 | 1021.5 | 1049 | 1076.5 | 1104.6667 | 1132.5 | 1160.3333 | 1188.5 | 1216 | 1244.3333 | 1272 | 1300 | 1327.3333 | 1351.001
| 7 | 1256 | 1290.8333 | 1325 | 1360 | 1395 | 1430 | 1464.6667 | 1499 | 1534 | 1569 | 1603.3333 | 1638 | 1672.6667 | 1701.0007
| 7.5 | 1557 | 1599.5 | 1642 | 1685.3333 | 1728 | 1770.5 | 1813 | 1855.5 | 1898 | 1941.3333 | 1984 | 2026 | 2069 | 2104.0006
| 8 | 1895.6667 | 1947.3333 | 1999 | 2050.6667 | 2102.3333 | 2154 | 2205.3333 | 2256.3333 | 2308 | 2359.6667 | 2410.6667 | 2462 | 2512.3333 | 2554.0005
| 8.5 | 2264.3333 | 2325.3333 | 2387 | 2447.8333 | 2508.6667 | 2569.5 | 2630.3333 | 2691 | 2751 | 2811 | 2870.3333 | 2930 | 2988 | 3035.0004
| 9 | 2648.3333 | 2719.1667 | 2790 | 2860.8333 | 2930.3333 | 2999.5 | 3068.3333 | 3136.3333 | 3203 | 3268 | 3332.3333 | 3395 | 3455 | 3504.0003
| 9.5 | 3033 | 3112.6667 | 3191 | 3268.5 | 3344 | 3418 | 3490 | 3559.3333 | 3626 | 3690.1667 | 3751 | 3809 | 3864 | 3907.0003
| 10 | 3403.6667 | 3487.3333 | 3569 | 3646.5 | 3721.3333 | 3792.5 | 3859.6667 | 3922.8333 | 3982 | 4035.3333 | 4085.3333 | 4133 | 4174 | 4207.0003
| 10.5 | 3740.6667 | 3821.3333 | 3898 | 3968.8333 | 4034.3333 | 4094.5 | 4149.3333 | 4199 | 4244 | 4283.1667 | 4317.6667 | 4349 | 4374.3333 | 4394.0002
| 11 | 4026 | 4096.8333 | 4161 | 4216.8333 | 4267.3333 | 4311.5 | 4349 | 4380.3333 | 4407 | 4425.3333 | 4439.6667 | 4452 | 4460 | 4467.0002
| 11.5 | 4246.3333 | 4300.1667 | 4346 | 4382.6667 | 4411.3333 | 4433 | 4449 | 4460.6667 | 4469 | 4474 | 4478.3333 | 4482 | 4484.6667 | 4487.0002
| 12 | 4394 | 4424.3333 | 4446 | 4460.1667 | 4469.6667 | 4476 | 4480.6667 | 4484.5 | 4487 | 4488.6667 | 4490.3333 | 4492 | 4492.3333 | 4494.0002
| 12.5 | 4462.3333 | 4472.3333 | 4479 | 4483.1667 | 4486.6667 | 4489 | 4490.6667 | 4492.1667 | 4493 | 4494.6667 | 4495.6667 | 4496 | 4496.3333 | 4498.0002
| 13 | 4483.6667 | 4487.5 | 4490 | 4491.6667 | 4493.3333 | 4494.5 | 4495.3333 | 4496.1667 | 4497 | 4497.8333 | 4498 | 4498 | 4498.3333 | 4500
| 13.5 | 4491.6667 | 4493.3333 | 4495 | 4495.8333 | 4496.6667 | 4497.5 | 4498 | 4498.1667 | 4499 | 4499 | 4499 | 4499 | 4499 | 4500
| 14 | 4495.3333 | 4496.1667 | 4497 | 4497.8333 | 4498.6667 | 4499 | 4499 | 4499 | 4499 | 4499 | 4499.6667 | 4500 | 4500 | 4500
| 14.5 | 4498 | 4498.1667 | 4499 | 4499 | 4499 | 4499 | 4499.3333 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 15 | 4499 | 4499 | 4499 | 4499 | 4499.6667 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 15.5 | 4499 | 4499.1667 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 16 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 16.5 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 17 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 17.5 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 18 | 4499 | 4499 | 4499 | 4499 | 4499 | 4499 | 4499 | 4499 | 4499 | 4499 | 4499 | 4499 | 4499 | 4499
| 18.5 | 4498 | 4498 | 4498 | 4498 | 4498 | 4498 | 4498 | 4498 | 4498 | 4498 | 4498 | 4498 | 4498 | 4498
| 19 | 4495 | 4495 | 4495 | 4495 | 4495 | 4495 | 4495 | 4495 | 4495 | 4495 | 4495 | 4495 | 4495 | 4495
| 19.5 | 4488 | 4488 | 4488 | 4488 | 4488 | 4488 | 4488 | 4488 | 4488 | 4488 | 4488 | 4488 | 4488 | 4488
| 20 | 4475 | 4475 | 4475 | 4475 | 4475 | 4475 | 4475 | 4475 | 4475 | 4475 | 4475 | 4475 | 4475 | 4475
| 20.5 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455
| 21 | 4425 | 4425 | 4425 | 4425 | 4425 | 4425 | 4425 | 4425 | 4425 | 4425 | 4425 | 4425 | 4425 | 4425
| 21.5 | 4386 | 4386 | 4386 | 4386 | 4386 | 4386 | 4386 | 4386 | 4386 | 4386 | 4386 | 4386 | 4386 | 4386
| 22 | 4337 | 4337 | 4337 | 4337 | 4337 | 4337 | 4337 | 4337 | 4337 | 4337 | 4337 | 4337 | 4337 | 4337
| 22.5 | 4281 | 4281 | 4281 | 4281 | 4281 | 4281 | 4281 | 4281 | 4281 | 4281 | 4281 | 4281 | 4281 | 4281

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948
| 3.5 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674
| 4 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438
| 4.5 | 0.82807 | 0.82822 | 0.8283 | 0.82838 | 0.82847 | 0.82855 | 0.82863 | 0.82872 | 0.8288 | 0.8288 | 0.82887 | 0.829 | 0.829 | 0.829
| 5 | 0.81813 | 0.81847 | 0.8188 | 0.81905 | 0.8193 | 0.81955 | 0.81977 | 0.81995 | 0.8202 | 0.82037 | 0.82053 | 0.8207 | 0.82077 | 0.8209
| 5.5 | 0.81553 | 0.81588 | 0.8163 | 0.81655 | 0.81687 | 0.81715 | 0.81737 | 0.81755 | 0.8178 | 0.81797 | 0.81813 | 0.8183 | 0.81837 | 0.8185
| 6 | 0.8166 | 0.81685 | 0.8171 | 0.81735 | 0.81753 | 0.8177 | 0.81787 | 0.81802 | 0.8181 | 0.81827 | 0.81837 | 0.8185 | 0.81853 | 0.8186
| 6.5 | 0.81797 | 0.81813 | 0.8183 | 0.81838 | 0.81847 | 0.8186 | 0.81873 | 0.81882 | 0.8189 | 0.81898 | 0.819 | 0.8191 | 0.81913 | 0.8192
| 7 | 0.81853 | 0.81862 | 0.8187 | 0.81878 | 0.81887 | 0.8189 | 0.81893 | 0.81902 | 0.8191 | 0.8191 | 0.81917 | 0.8192 | 0.81923 | 0.8193
| 7.5 | 0.81643 | 0.81652 | 0.8166 | 0.8166 | 0.81667 | 0.81675 | 0.8168 | 0.8168 | 0.8168 | 0.81688 | 0.8169 | 0.8169 | 0.8169 | 0.8169
| 8 | 0.80723 | 0.8073 | 0.8073 | 0.80738 | 0.8074 | 0.8074 | 0.8074 | 0.8074 | 0.8074 | 0.80732 | 0.80723 | 0.8071 | 0.80693 | 0.8068
| 8.5 | 0.7859 | 0.7859 | 0.7859 | 0.78582 | 0.7858 | 0.7857 | 0.78553 | 0.78532 | 0.7849 | 0.7844 | 0.78377 | 0.783 | 0.78193 | 0.781
| 9 | 0.75127 | 0.75117 | 0.751 | 0.75075 | 0.7503 | 0.74965 | 0.74877 | 0.74762 | 0.7462 | 0.74437 | 0.74213 | 0.7396 | 0.7366 | 0.734
| 9.5 | 0.7067 | 0.70613 | 0.7053 | 0.70413 | 0.70257 | 0.7005 | 0.69797 | 0.69498 | 0.6914 | 0.68723 | 0.68253 | 0.6774 | 0.6718 | 0.667
| 10 | 0.656 | 0.65415 | 0.6519 | 0.6489 | 0.64537 | 0.6411 | 0.63617 | 0.63067 | 0.6245 | 0.61775 | 0.61067 | 0.6031 | 0.59537 | 0.5889
| 10.5 | 0.60147 | 0.59772 | 0.5933 | 0.58797 | 0.58203 | 0.5754 | 0.56817 | 0.56047 | 0.5523 | 0.5438 | 0.53517 | 0.5263 | 0.5174 | 0.5102
| 11 | 0.54483 | 0.53877 | 0.5321 | 0.52477 | 0.5169 | 0.50855 | 0.49987 | 0.49098 | 0.4819 | 0.47273 | 0.46363 | 0.4546 | 0.44577 | 0.4387
| 11.5 | 0.488 | 0.48015 | 0.4719 | 0.46323 | 0.45437 | 0.44535 | 0.43623 | 0.4271 | 0.4181 | 0.40927 | 0.40057 | 0.3921 | 0.3839 | 0.3775
| 12 | 0.4334 | 0.42462 | 0.4157 | 0.4067 | 0.3977 | 0.38875 | 0.37997 | 0.37142 | 0.363 | 0.35492 | 0.3471 | 0.3395 | 0.33227 | 0.3266
| 12.5 | 0.38323 | 0.37432 | 0.3654 | 0.35673 | 0.3482 | 0.3399 | 0.33187 | 0.3241 | 0.3166 | 0.30943 | 0.3026 | 0.2959 | 0.28963 | 0.2847
| 13 | 0.33863 | 0.33003 | 0.3217 | 0.3137 | 0.30597 | 0.2985 | 0.29133 | 0.28448 | 0.2779 | 0.27165 | 0.26567 | 0.2599 | 0.25437 | 0.2501
| 13.5 | 0.29983 | 0.29197 | 0.2843 | 0.27713 | 0.27023 | 0.26365 | 0.25737 | 0.25133 | 0.2455 | 0.24008 | 0.23487 | 0.2298 | 0.22507 | 0.2214
| 14 | 0.2665 | 0.25935 | 0.2526 | 0.24618 | 0.2401 | 0.23425 | 0.22867 | 0.22338 | 0.2183 | 0.21355 | 0.209 | 0.2046 | 0.2004 | 0.1972
| 14.5 | 0.23793 | 0.2316 | 0.2256 | 0.21993 | 0.21453 | 0.20935 | 0.20443 | 0.1998 | 0.1953 | 0.19105 | 0.18707 | 0.1832 | 0.17947 | 0.1766
| 15 | 0.2135 | 0.20783 | 0.2025 | 0.19742 | 0.1926 | 0.18805 | 0.18373 | 0.1796 | 0.1756 | 0.17185 | 0.1683 | 0.1649 | 0.16163 | 0.1591
| 15.5 | 0.19247 | 0.18743 | 0.1826 | 0.1781 | 0.17387 | 0.1698 | 0.1659 | 0.1622 | 0.1587 | 0.15537 | 0.15217 | 0.1491 | 0.14617 | 0.1439
| 16 | 0.17427 | 0.16973 | 0.1654 | 0.1614 | 0.1576 | 0.15395 | 0.15047 | 0.14717 | 0.144 | 0.141 | 0.13813 | 0.1354 | 0.13277 | 0.1307
| 16.5 | 0.15843 | 0.15433 | 0.1505 | 0.14683 | 0.14337 | 0.1401 | 0.137 | 0.13403 | 0.1312 | 0.12845 | 0.12583 | 0.1234 | 0.121 | 0.1192
| 17 | 0.1446 | 0.1409 | 0.1374 | 0.13415 | 0.13103 | 0.12805 | 0.1252 | 0.12248 | 0.1199 | 0.11748 | 0.11513 | 0.1128 | 0.11067 | 0.109
| 17.5 | 0.13237 | 0.12907 | 0.1259 | 0.1229 | 0.12003 | 0.11735 | 0.1148 | 0.11233 | 0.11 | 0.10775 | 0.10563 | 0.1036 | 0.10163 | 0.1001
| 18 | 0.12157 | 0.11852 | 0.1156 | 0.11293 | 0.11033 | 0.10785 | 0.1055 | 0.10328 | 0.1012 | 0.099117 | 0.097167 | 0.0953 | 0.0935 | 0.0921
| 18.5 | 0.11197 | 0.10918 | 0.1066 | 0.1041 | 0.10173 | 0.09945 | 0.0973 | 0.0953 | 0.0933 | 0.091467 | 0.0897 | 0.088 | 0.086367 | 0.0851
| 19 | 0.10337 | 0.10082 | 0.0984 | 0.09615 | 0.093967 | 0.0919 | 0.089933 | 0.08805 | 0.0863 | 0.08455 | 0.082933 | 0.0814 | 0.079833 | 0.0787
| 19.5 | 0.095633 | 0.093267 | 0.0911 | 0.089017 | 0.087 | 0.0851 | 0.0833 | 0.081567 | 0.0799 | 0.078317 | 0.0768 | 0.0754 | 0.073967 | 0.0729
| 20 | 0.088533 | 0.0864 | 0.0844 | 0.082483 | 0.080633 | 0.0789 | 0.077233 | 0.0756 | 0.0741 | 0.072683 | 0.071267 | 0.0699 | 0.0687 | 0.0677
| 20.5 | 0.0821 | 0.080133 | 0.0783 | 0.076467 | 0.074767 | 0.0732 | 0.0717 | 0.070217 | 0.0688 | 0.067467 | 0.0662 | 0.065 | 0.063767 | 0.0629
| 21 | 0.076167 | 0.07435 | 0.0726 | 0.070933 | 0.0694 | 0.06795 | 0.066533 | 0.06515 | 0.0639 | 0.06265 | 0.061467 | 0.0603 | 0.059267 | 0.0584
| 21.5 | 0.070633 | 0.068983 | 0.0674 | 0.0659 | 0.064467 | 0.0631 | 0.0618 | 0.06055 | 0.0593 | 0.058217 | 0.057133 | 0.0561 | 0.0551 | 0.0543
| 22 | 0.065567 | 0.064 | 0.0625 | 0.061167 | 0.059833 | 0.05855 | 0.057333 | 0.056183 | 0.0551 | 0.0541 | 0.0531 | 0.0521 | 0.051233 | 0.0505
| 22.5 | 0.060833 | 0.059433 | 0.0581 | 0.056767 | 0.055567 | 0.0544 | 0.0533 | 0.052283 | 0.0512 | 0.050283 | 0.049367 | 0.0485 | 0.047667 | 0.047
|  | 0.056567 | 0.05525 | 0.054 | 0.052833 | 0.051733 | 0.05065 | 0.0496 | 0.048617 | 0.0477 | 0.046783 | 0.045933 | 0.0451 | 0.044367 | 0.0437
|  | 0.0527 | 0.051467 | 0.0503 | 0.049217 | 0.0482 | 0.0472 | 0.046233 | 0.045333 | 0.0445 | 0.043667 | 0.042833 | 0.0421 | 0.0414 | 0.0408
|  | 0.049233 | 0.048083 | 0.047 | 0.046 | 0.045 | 0.0441 | 0.043233 | 0.04235 | 0.0416 | 0.04085 | 0.0401 | 0.0394 | 0.038733 | 0.0382
|  | 0.046067 | 0.045 | 0.044 | 0.043083 | 0.042167 | 0.0413 | 0.040467 | 0.03965 | 0.0389 | 0.038233 | 0.037567 | 0.0369 | 0.036267 | 0.0358
|  | 0.0433 | 0.042317 | 0.0414 | 0.040483 | 0.039633 | 0.03885 | 0.0381 | 0.03735 | 0.0366 | 0.035933 | 0.035333 | 0.0347 | 0.034167 | 0.0337
|  | 0.0408 | 0.039833 | 0.039 | 0.038167 | 0.037333 | 0.0366 | 0.0359 | 0.035167 | 0.0345 | 0.033917 | 0.033333 | 0.0327 | 0.0322 | 0.0318
|  | 0.038533 | 0.037633 | 0.0368 | 0.03605 | 0.0353 | 0.0346 | 0.033933 | 0.033267 | 0.0326 | 0.032017 | 0.0315 | 0.0309 | 0.0304 | 0.03
|  | 0.036567 | 0.035733 | 0.0349 | 0.03415 | 0.033467 | 0.0328 | 0.032167 | 0.031583 | 0.031 | 0.030417 | 0.0299 | 0.0294 | 0.0289 | 0.0285
|  | 0.0347 | 0.03395 | 0.0332 | 0.03245 | 0.031833 | 0.0312 | 0.030567 | 0.029983 | 0.0294 | 0.0289 | 0.0284 | 0.0279 | 0.027433 | 0.0271