## Sheet1
PROPERTIES
General
Name | Gamesa SG 5.0-145 -MOD 4,6 MW
Manufacturer | Gamesa
Hub Height | 91 | 95.5 | 97.5 | 127.5
Power
Rated Power | 4600
Peak Power | 4600
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 145
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 27
Restart Wind Speed | 24
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -30
Low Temperature Restart | -20
High Temperature Shutdown | 50
High Temperature Restart | 45
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | II
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 8.5
Vref | 42.5
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.94 | 0.97 | 1 | 1.03 | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.24 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 30 | 33 | 36 | 38 | 41 | 44 | 46 | 49 | 52 | 54 | 56 | 57 | 60
| 3.5 | 86 | 90 | 95 | 100 | 104 | 109 | 113 | 118 | 123 | 127 | 130 | 132 | 137
| 4 | 170 | 178 | 185 | 192 | 200 | 207 | 215 | 222 | 230 | 237 | 241 | 245 | 252
| 4.5 | 278 | 289 | 300 | 311 | 322 | 333 | 344 | 355 | 366 | 377 | 383 | 388 | 399
| 5 | 410 | 425 | 441 | 456 | 471 | 486 | 502 | 517 | 532 | 547 | 555 | 563 | 578
| 5.5 | 569 | 590 | 610 | 630 | 651 | 671 | 691 | 711 | 732 | 752 | 762 | 772 | 792
| 6 | 759 | 785 | 812 | 838 | 864 | 891 | 917 | 943 | 969 | 996 | 1009 | 1022 | 1048
| 6.5 | 982 | 1016 | 1049 | 1082 | 1116 | 1149 | 1183 | 1216 | 1250 | 1283 | 1300 | 1316 | 1350
| 7 | 1242 | 1284 | 1325 | 1367 | 1409 | 1451 | 1492 | 1534 | 1576 | 1617 | 1638 | 1659 | 1700
| 7.5 | 1540 | 1591 | 1642 | 1694 | 1745 | 1796 | 1847 | 1898 | 1950 | 2001 | 2026 | 2052 | 2103
| 8 | 1875 | 1937 | 1999 | 2061 | 2123 | 2185 | 2246 | 2308 | 2370 | 2431 | 2462 | 2493 | 2554
| 8.5 | 2240 | 2313 | 2387 | 2460 | 2533 | 2606 | 2679 | 2752 | 2824 | 2896 | 2931 | 2967 | 3037
| 9 | 2620 | 2706 | 2790 | 2875 | 2959 | 3043 | 3126 | 3207 | 3287 | 3364 | 3403 | 3440 | 3514
| 9.5 | 3002 | 3098 | 3193 | 3287 | 3379 | 3469 | 3555 | 3639 | 3718 | 3794 | 3830 | 3866 | 3933
| 10 | 3373 | 3476 | 3576 | 3673 | 3765 | 3852 | 3934 | 4010 | 4080 | 4143 | 4173 | 4201 | 4254
| 10.5 | 3718 | 3821 | 3917 | 4007 | 4090 | 4165 | 4232 | 4292 | 4345 | 4390 | 4411 | 4430 | 4463
| 11 | 4020 | 4113 | 4196 | 4270 | 4335 | 4392 | 4439 | 4477 | 4507 | 4528 | 4537 | 4545 | 4557
| 11.5 | 4264 | 4338 | 4401 | 4454 | 4495 | 4525 | 4546 | 4559 | 4569 | 4575 | 4578 | 4580 | 4583
| 12 | 4441 | 4490 | 4526 | 4549 | 4564 | 4573 | 4579 | 4584 | 4587 | 4589 | 4590 | 4591 | 4592
| 12.5 | 4541 | 4561 | 4573 | 4580 | 4585 | 4588 | 4590 | 4592 | 4593 | 4595 | 4595 | 4596 | 4596
| 13 | 4577 | 4583 | 4587 | 4590 | 4592 | 4594 | 4595 | 4596 | 4597 | 4598 | 4598 | 4598 | 4598
| 13.5 | 4588 | 4591 | 4593 | 4595 | 4596 | 4597 | 4598 | 4598 | 4599 | 4599 | 4599 | 4599 | 4599
| 14 | 4594 | 4595 | 4597 | 4598 | 4598 | 4599 | 4599 | 4599 | 4599 | 4599 | 4599 | 4600 | 4600
| 14.5 | 4597 | 4598 | 4598 | 4599 | 4599 | 4599 | 4599 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600
| 15 | 4598 | 4599 | 4599 | 4599 | 4599 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600
| 15.5 | 4599 | 4599 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600
| 16 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600
| 16.5 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600
| 17 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600
| 17.5 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600 | 4600
| 18 | 4599 | 4599 | 4599 | 4599 | 4599 | 4599 | 4599 | 4599 | 4599 | 4599 | 4599 | 4599 | 4599
| 18.5 | 4598 | 4598 | 4598 | 4598 | 4598 | 4598 | 4598 | 4598 | 4598 | 4598 | 4598 | 4598 | 4598
| 19 | 4594 | 4594 | 4594 | 4594 | 4594 | 4594 | 4594 | 4594 | 4594 | 4594 | 4594 | 4594 | 4594
| 19.5 | 4586 | 4586 | 4586 | 4586 | 4586 | 4586 | 4586 | 4586 | 4586 | 4586 | 4586 | 4586 | 4586
| 20 | 4571 | 4571 | 4571 | 4571 | 4571 | 4571 | 4571 | 4571 | 4571 | 4571 | 4571 | 4571 | 4571
| 20.5 | 4548 | 4548 | 4548 | 4548 | 4548 | 4548 | 4548 | 4548 | 4548 | 4548 | 4548 | 4548 | 4548
| 21 | 4514 | 4514 | 4514 | 4514 | 4514 | 4514 | 4514 | 4514 | 4514 | 4514 | 4514 | 4514 | 4514
| 21.5 | 4469 | 4469 | 4469 | 4469 | 4469 | 4469 | 4469 | 4469 | 4469 | 4469 | 4469 | 4469 | 4469
| 22 | 4414 | 4413 | 4413 | 4414 | 4414 | 4414 | 4413 | 4414 | 4414 | 4413 | 4414 | 4414 | 4413
| 22.5 | 4351 | 4351 | 4351 | 4351 | 4351 | 4351 | 4351 | 4351 | 4351 | 4351 | 4351 | 4351 | 4351
| 23 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283
| 23.5 | 4214 | 4214 | 4214 | 4214 | 4214 | 4214 | 4214 | 4214 | 4214 | 4214 | 4214 | 4214 | 4214
| 24 | 4147 | 4146 | 4146 | 4147 | 4147 | 4147 | 4146 | 4146 | 4147 | 4146 | 4147 | 4146 | 4146
| 24.5 | 4081 | 4081 | 4081 | 4081 | 4081 | 4081 | 4081 | 4081 | 4081 | 4081 | 4081 | 4081 | 4081
| 25 | 4025 | 4025 | 4024 | 4025 | 4025 | 4025 | 4024 | 4025 | 4025 | 4025 | 4025 | 4025 | 4024
| 25.5 | 3971 | 3971 | 3971 | 3971 | 3971 | 3971 | 3971 | 3971 | 3971 | 3971 | 3971 | 3971 | 3971
| 26 | 3923 | 3923 | 3923 | 3923 | 3923 | 3923 | 3923 | 3923 | 3923 | 3923 | 3923 | 3923 | 3923
| 26.5 | 3883 | 3883 | 3883 | 3883 | 3883 | 3883 | 3883 | 3883 | 3883 | 3883 | 3883 | 3883 | 3883
| 27 | 3848 | 3848 | 3848 | 3848 | 3848 | 3848 | 3848 | 3848 | 3848 | 3848 | 3848 | 3848 | 3848

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.94 | 0.97 | 1 | 1.03 | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.24 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948
| 3.5 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674
| 4 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438
| 4.5 | 0.828 | 0.8282 | 0.8283 | 0.8284 | 0.8285 | 0.8286 | 0.8287 | 0.8288 | 0.8288 | 0.8289 | 0.829 | 0.829 | 0.829
| 5 | 0.818 | 0.8184 | 0.8188 | 0.8191 | 0.8194 | 0.8197 | 0.8199 | 0.8202 | 0.8204 | 0.8206 | 0.8207 | 0.8207 | 0.8209
| 5.5 | 0.8154 | 0.8158 | 0.8163 | 0.8166 | 0.817 | 0.8173 | 0.8175 | 0.8178 | 0.818 | 0.8182 | 0.8183 | 0.8183 | 0.8185
| 6 | 0.8165 | 0.8168 | 0.8171 | 0.8174 | 0.8176 | 0.8178 | 0.818 | 0.8181 | 0.8183 | 0.8184 | 0.8185 | 0.8185 | 0.8186
| 6.5 | 0.8179 | 0.8181 | 0.8183 | 0.8184 | 0.8185 | 0.8187 | 0.8188 | 0.8189 | 0.819 | 0.819 | 0.8191 | 0.8191 | 0.8192
| 7 | 0.8185 | 0.8186 | 0.8187 | 0.8188 | 0.8189 | 0.8189 | 0.819 | 0.8191 | 0.8191 | 0.8192 | 0.8192 | 0.8192 | 0.8193
| 7.5 | 0.8164 | 0.8165 | 0.8166 | 0.8166 | 0.8167 | 0.8168 | 0.8168 | 0.8168 | 0.8169 | 0.8169 | 0.8169 | 0.8169 | 0.817
| 8 | 0.8072 | 0.8073 | 0.8073 | 0.8074 | 0.8074 | 0.8074 | 0.8074 | 0.8074 | 0.8074 | 0.8073 | 0.8073 | 0.8072 | 0.807
| 8.5 | 0.7859 | 0.7859 | 0.7859 | 0.7859 | 0.7858 | 0.7858 | 0.7856 | 0.7853 | 0.7849 | 0.7843 | 0.7839 | 0.7835 | 0.7823
| 9 | 0.7514 | 0.7513 | 0.7512 | 0.751 | 0.7506 | 0.7499 | 0.749 | 0.7477 | 0.7459 | 0.7437 | 0.7423 | 0.741 | 0.7377
| 9.5 | 0.7072 | 0.7068 | 0.7061 | 0.705 | 0.7035 | 0.7014 | 0.6986 | 0.695 | 0.6907 | 0.6858 | 0.6829 | 0.6801 | 0.6737
| 10 | 0.6577 | 0.6562 | 0.654 | 0.6511 | 0.6474 | 0.6428 | 0.6372 | 0.6307 | 0.6234 | 0.6155 | 0.6112 | 0.607 | 0.5979
| 10.5 | 0.6054 | 0.6018 | 0.5973 | 0.5918 | 0.5853 | 0.5779 | 0.5696 | 0.5605 | 0.5509 | 0.541 | 0.5358 | 0.5307 | 0.5203
| 11 | 0.5514 | 0.5453 | 0.5381 | 0.53 | 0.5212 | 0.5116 | 0.5015 | 0.491 | 0.4804 | 0.4697 | 0.4643 | 0.4591 | 0.4485
| 11.5 | 0.497 | 0.4885 | 0.4792 | 0.4694 | 0.4591 | 0.4486 | 0.4379 | 0.4272 | 0.4166 | 0.4063 | 0.4012 | 0.3962 | 0.3864
| 12 | 0.444 | 0.4339 | 0.4236 | 0.413 | 0.4024 | 0.3919 | 0.3815 | 0.3714 | 0.3616 | 0.3522 | 0.3476 | 0.3432 | 0.3345
| 12.5 | 0.3943 | 0.3837 | 0.3732 | 0.3628 | 0.3526 | 0.3428 | 0.3333 | 0.3241 | 0.3154 | 0.3071 | 0.303 | 0.2991 | 0.2916
| 13 | 0.3494 | 0.339 | 0.329 | 0.3193 | 0.31 | 0.3011 | 0.2926 | 0.2845 | 0.2768 | 0.2695 | 0.266 | 0.2626 | 0.2561
| 13.5 | 0.3099 | 0.3002 | 0.291 | 0.2822 | 0.2738 | 0.2659 | 0.2584 | 0.2513 | 0.2446 | 0.2382 | 0.2352 | 0.2322 | 0.2265
| 14 | 0.2756 | 0.2668 | 0.2585 | 0.2507 | 0.2432 | 0.2363 | 0.2297 | 0.2234 | 0.2175 | 0.212 | 0.2093 | 0.2067 | 0.2017
| 14.5 | 0.2461 | 0.2382 | 0.2308 | 0.2238 | 0.2173 | 0.2111 | 0.2053 | 0.1998 | 0.1946 | 0.1897 | 0.1873 | 0.185 | 0.1806
| 15 | 0.2208 | 0.2138 | 0.2071 | 0.2009 | 0.1951 | 0.1896 | 0.1845 | 0.1796 | 0.175 | 0.1706 | 0.1685 | 0.1665 | 0.1626
| 15.5 | 0.199 | 0.1927 | 0.1868 | 0.1813 | 0.1761 | 0.1712 | 0.1666 | 0.1622 | 0.1581 | 0.1542 | 0.1524 | 0.1505 | 0.147
| 16 | 0.1801 | 0.1745 | 0.1692 | 0.1642 | 0.1596 | 0.1552 | 0.1511 | 0.1472 | 0.1435 | 0.14 | 0.1383 | 0.1367 | 0.1335
| 16.5 | 0.1637 | 0.1586 | 0.1538 | 0.1494 | 0.1452 | 0.1412 | 0.1375 | 0.134 | 0.1307 | 0.1276 | 0.126 | 0.1246 | 0.1217
| 17 | 0.1493 | 0.1447 | 0.1404 | 0.1364 | 0.1326 | 0.129 | 0.1257 | 0.1225 | 0.1195 | 0.1166 | 0.1153 | 0.1139 | 0.1114
| 17.5 | 0.1367 | 0.1325 | 0.1286 | 0.1249 | 0.1215 | 0.1183 | 0.1152 | 0.1123 | 0.1096 | 0.107 | 0.1058 | 0.1045 | 0.1022
| 18 | 0.1255 | 0.1217 | 0.1182 | 0.1148 | 0.1117 | 0.1087 | 0.1059 | 0.1033 | 0.1008 | 0.0985 | 0.0973 | 0.0962 | 0.0941
| 18.5 | 0.1156 | 0.1121 | 0.1088 | 0.1058 | 0.1029 | 0.1002 | 0.0977 | 0.0953 | 0.093 | 0.0908 | 0.0898 | 0.0888 | 0.0868
| 19 | 0.1066 | 0.1035 | 0.1005 | 0.0977 | 0.0951 | 0.0926 | 0.0903 | 0.0881 | 0.086 | 0.084 | 0.083 | 0.0821 | 0.0803
| 19.5 | 0.0986 | 0.0957 | 0.093 | 0.0904 | 0.088 | 0.0857 | 0.0836 | 0.0815 | 0.0796 | 0.0778 | 0.0769 | 0.0761 | 0.0744
| 20 | 0.0913 | 0.0886 | 0.0861 | 0.0838 | 0.0815 | 0.0794 | 0.0775 | 0.0756 | 0.0738 | 0.0721 | 0.0713 | 0.0706 | 0.069
| 20.5 | 0.0846 | 0.0821 | 0.0798 | 0.0776 | 0.0756 | 0.0737 | 0.0719 | 0.0701 | 0.0685 | 0.067 | 0.0662 | 0.0655 | 0.0641
| 21 | 0.0784 | 0.0761 | 0.074 | 0.072 | 0.0701 | 0.0683 | 0.0667 | 0.0651 | 0.0636 | 0.0621 | 0.0615 | 0.0608 | 0.0595
| 21.5 | 0.0726 | 0.0705 | 0.0686 | 0.0667 | 0.065 | 0.0634 | 0.0618 | 0.0604 | 0.059 | 0.0577 | 0.0571 | 0.0564 | 0.0552
| 22 | 0.0673 | 0.0654 | 0.0636 | 0.0619 | 0.0603 | 0.0588 | 0.0574 | 0.056 | 0.0547 | 0.0535 | 0.053 | 0.0524 | 0.0513
| 22.5 | 0.0624 | 0.0606 | 0.059 | 0.0574 | 0.0559 | 0.0546 | 0.0533 | 0.052 | 0.0508 | 0.0497 | 0.0492 | 0.0487 | 0.0477
| 23 | 0.0579 | 0.0563 | 0.0548 | 0.0533 | 0.052 | 0.0507 | 0.0495 | 0.0483 | 0.0473 | 0.0462 | 0.0457 | 0.0453 | 0.0443
| 23.5 | 0.0539 | 0.0524 | 0.051 | 0.0496 | 0.0484 | 0.0472 | 0.0461 | 0.045 | 0.044 | 0.0431 | 0.0426 | 0.0422 | 0.0413
| 24 | 0.0503 | 0.0489 | 0.0475 | 0.0463 | 0.0451 | 0.044 | 0.043 | 0.042 | 0.0411 | 0.0402 | 0.0398 | 0.0394 | 0.0386
| 24.5 | 0.047 | 0.0457 | 0.0444 | 0.0433 | 0.0422 | 0.0412 | 0.0402 | 0.0393 | 0.0385 | 0.0376 | 0.0372 | 0.0369 | 0.0361
| 25 | 0.0441 | 0.0429 | 0.0417 | 0.0407 | 0.0396 | 0.0387 | 0.0378 | 0.0369 | 0.0361 | 0.0354 | 0.035 | 0.0346 | 0.0339
| 25.5 | 0.0415 | 0.0403 | 0.0393 | 0.0383 | 0.0373 | 0.0364 | 0.0356 | 0.0348 | 0.034 | 0.0333 | 0.033 | 0.0326 | 0.032
| 26 | 0.0392 | 0.0381 | 0.0371 | 0.0361 | 0.0352 | 0.0344 | 0.0336 | 0.0329 | 0.0321 | 0.0315 | 0.0311 | 0.0308 | 0.0302
| 26.5 | 0.0371 | 0.0361 | 0.0351 | 0.0342 | 0.0334 | 0.0326 | 0.0318 | 0.0311 | 0.0305 | 0.0298 | 0.0295 | 0.0292 | 0.0287
| 27 | 0.0352 | 0.0343 | 0.0334 | 0.0325 | 0.0317 | 0.031 | 0.0303 | 0.0296 | 0.029 | 0.0283 | 0.0281 | 0.0278 | 0.0272