## Sheet1
PROPERTIES
General
Name | Gamesa SG 5.0-145 -MOD 4,8 MW
Manufacturer | Gamesa
Hub Height | 91 | 95.5 | 97.5 | 127.5
Power
Rated Power | 4800
Peak Power | 4800
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 145
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 27
Restart Wind Speed | 24
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -30
Low Temperature Restart | -20
High Temperature Shutdown | 50
High Temperature Restart | 45
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | II
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 8.5
Vref | 42.5
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.94 | 0.97 | 1 | 1.03 | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.24 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 30 | 33 | 36 | 38 | 41 | 44 | 46 | 49 | 52 | 54 | 56 | 57 | 60
| 3.5 | 86 | 90 | 95 | 100 | 104 | 109 | 113 | 118 | 123 | 127 | 130 | 132 | 137
| 4 | 170 | 178 | 185 | 192 | 200 | 207 | 215 | 222 | 230 | 237 | 241 | 245 | 252
| 4.5 | 278 | 289 | 300 | 311 | 322 | 333 | 344 | 355 | 366 | 377 | 383 | 388 | 399
| 5 | 410 | 425 | 441 | 456 | 471 | 486 | 502 | 517 | 532 | 547 | 555 | 563 | 578
| 5.5 | 569 | 590 | 610 | 630 | 651 | 671 | 691 | 711 | 732 | 752 | 762 | 772 | 792
| 6 | 759 | 785 | 812 | 838 | 864 | 891 | 917 | 943 | 969 | 996 | 1009 | 1022 | 1048
| 6.5 | 982 | 1016 | 1049 | 1082 | 1116 | 1149 | 1183 | 1216 | 1250 | 1283 | 1300 | 1316 | 1350
| 7 | 1242 | 1284 | 1325 | 1367 | 1409 | 1451 | 1492 | 1534 | 1576 | 1617 | 1638 | 1659 | 1700
| 7.5 | 1540 | 1591 | 1642 | 1694 | 1745 | 1796 | 1847 | 1898 | 1950 | 2001 | 2026 | 2052 | 2103
| 8 | 1875 | 1937 | 1999 | 2061 | 2123 | 2185 | 2246 | 2308 | 2370 | 2431 | 2462 | 2493 | 2554
| 8.5 | 2240 | 2313 | 2387 | 2460 | 2533 | 2606 | 2680 | 2752 | 2825 | 2897 | 2933 | 2969 | 3041
| 9 | 2620 | 2706 | 2791 | 2876 | 2960 | 3045 | 3129 | 3212 | 3294 | 3374 | 3414 | 3453 | 3530
| 9.5 | 3003 | 3099 | 3196 | 3291 | 3385 | 3478 | 3569 | 3657 | 3742 | 3824 | 3864 | 3902 | 3977
| 10 | 3377 | 3483 | 3587 | 3688 | 3786 | 3880 | 3970 | 4054 | 4133 | 4207 | 4241 | 4274 | 4336
| 10.5 | 3732 | 3841 | 3946 | 4044 | 4137 | 4223 | 4302 | 4373 | 4437 | 4494 | 4520 | 4544 | 4588
| 11 | 4055 | 4158 | 4254 | 4341 | 4418 | 4488 | 4548 | 4600 | 4644 | 4680 | 4695 | 4707 | 4728
| 11.5 | 4329 | 4417 | 4495 | 4563 | 4620 | 4667 | 4704 | 4729 | 4748 | 4760 | 4765 | 4769 | 4775
| 12 | 4541 | 4609 | 4664 | 4706 | 4735 | 4754 | 4767 | 4775 | 4780 | 4784 | 4785 | 4787 | 4789
| 12.5 | 4687 | 4726 | 4751 | 4766 | 4775 | 4781 | 4785 | 4788 | 4790 | 4792 | 4793 | 4793 | 4795
| 13 | 4758 | 4772 | 4780 | 4785 | 4788 | 4791 | 4793 | 4794 | 4795 | 4796 | 4797 | 4797 | 4798
| 13.5 | 4782 | 4786 | 4790 | 4792 | 4794 | 4795 | 4796 | 4797 | 4798 | 4798 | 4798 | 4799 | 4799
| 14 | 4790 | 4793 | 4795 | 4796 | 4797 | 4798 | 4798 | 4799 | 4799 | 4799 | 4799 | 4799 | 4799
| 14.5 | 4795 | 4796 | 4797 | 4798 | 4798 | 4799 | 4799 | 4799 | 4799 | 4800 | 4800 | 4800 | 4800
| 15 | 4797 | 4798 | 4799 | 4799 | 4799 | 4799 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800
| 15.5 | 4799 | 4799 | 4799 | 4799 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800
| 16 | 4799 | 4799 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800
| 16.5 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800
| 17 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800
| 17.5 | 4799 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800
| 18 | 4799 | 4799 | 4799 | 4799 | 4799 | 4799 | 4799 | 4799 | 4799 | 4799 | 4799 | 4799 | 4799
| 18.5 | 4797 | 4797 | 4797 | 4797 | 4797 | 4797 | 4797 | 4797 | 4797 | 4797 | 4797 | 4797 | 4797
| 19 | 4792 | 4792 | 4792 | 4792 | 4792 | 4792 | 4792 | 4792 | 4792 | 4792 | 4792 | 4792 | 4792
| 19.5 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782
| 20 | 4763 | 4763 | 4763 | 4763 | 4763 | 4763 | 4763 | 4763 | 4763 | 4763 | 4763 | 4763 | 4763
| 20.5 | 4734 | 4734 | 4734 | 4734 | 4734 | 4734 | 4734 | 4734 | 4734 | 4734 | 4734 | 4734 | 4734
| 21 | 4692 | 4692 | 4692 | 4692 | 4692 | 4692 | 4692 | 4692 | 4692 | 4692 | 4692 | 4692 | 4692
| 21.5 | 4635 | 4635 | 4635 | 4635 | 4635 | 4635 | 4635 | 4635 | 4635 | 4635 | 4635 | 4635 | 4635
| 22 | 4567 | 4567 | 4567 | 4567 | 4567 | 4567 | 4567 | 4567 | 4567 | 4567 | 4567 | 4567 | 4567
| 22.5 | 4489 | 4490 | 4490 | 4490 | 4490 | 4490 | 4489 | 4489 | 4490 | 4490 | 4490 | 4490 | 4489
| 23 | 4407 | 4407 | 4407 | 4407 | 4407 | 4407 | 4407 | 4407 | 4407 | 4407 | 4407 | 4407 | 4407
| 23.5 | 4323 | 4323 | 4323 | 4323 | 4323 | 4323 | 4323 | 4323 | 4323 | 4323 | 4323 | 4323 | 4323
| 24 | 4242 | 4242 | 4242 | 4242 | 4242 | 4242 | 4242 | 4242 | 4242 | 4242 | 4242 | 4242 | 4242
| 24.5 | 4164 | 4164 | 4164 | 4164 | 4164 | 4164 | 4164 | 4164 | 4164 | 4164 | 4164 | 4164 | 4164
| 25 | 4096 | 4097 | 4096 | 4097 | 4097 | 4097 | 4096 | 4096 | 4097 | 4097 | 4097 | 4096 | 4096
| 25.5 | 4034 | 4034 | 4034 | 4034 | 4034 | 4034 | 4034 | 4034 | 4034 | 4034 | 4034 | 4034 | 4034
| 26 | 3977 | 3977 | 3977 | 3977 | 3977 | 3977 | 3977 | 3977 | 3977 | 3977 | 3977 | 3977 | 3977
| 26.5 | 3930 | 3931 | 3930 | 3931 | 3930 | 3930 | 3930 | 3930 | 3931 | 3930 | 3931 | 3930 | 3930
| 27 | 3889 | 3889 | 3889 | 3889 | 3889 | 3889 | 3889 | 3889 | 3889 | 3889 | 3889 | 3889 | 3889

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.94 | 0.97 | 1 | 1.03 | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.24 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948
| 3.5 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674 | 0.8674
| 4 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438
| 4.5 | 0.828 | 0.8282 | 0.8283 | 0.8284 | 0.8285 | 0.8286 | 0.8287 | 0.8288 | 0.8288 | 0.8289 | 0.829 | 0.829 | 0.829
| 5 | 0.818 | 0.8184 | 0.8188 | 0.8191 | 0.8194 | 0.8197 | 0.8199 | 0.8202 | 0.8204 | 0.8206 | 0.8207 | 0.8207 | 0.8209
| 5.5 | 0.8154 | 0.8158 | 0.8163 | 0.8166 | 0.817 | 0.8173 | 0.8175 | 0.8178 | 0.818 | 0.8182 | 0.8183 | 0.8183 | 0.8185
| 6 | 0.8165 | 0.8168 | 0.8171 | 0.8174 | 0.8176 | 0.8178 | 0.818 | 0.8181 | 0.8183 | 0.8184 | 0.8185 | 0.8185 | 0.8186
| 6.5 | 0.8179 | 0.8181 | 0.8183 | 0.8184 | 0.8185 | 0.8187 | 0.8188 | 0.8189 | 0.819 | 0.819 | 0.8191 | 0.8191 | 0.8192
| 7 | 0.8185 | 0.8186 | 0.8187 | 0.8188 | 0.8189 | 0.8189 | 0.819 | 0.8191 | 0.8191 | 0.8192 | 0.8192 | 0.8192 | 0.8193
| 7.5 | 0.8164 | 0.8165 | 0.8166 | 0.8166 | 0.8167 | 0.8168 | 0.8168 | 0.8168 | 0.8169 | 0.8169 | 0.8169 | 0.817 | 0.817
| 8 | 0.8072 | 0.8073 | 0.8073 | 0.8074 | 0.8074 | 0.8074 | 0.8075 | 0.8075 | 0.8075 | 0.8075 | 0.8075 | 0.8074 | 0.8074
| 8.5 | 0.7859 | 0.7859 | 0.7859 | 0.7859 | 0.7859 | 0.7859 | 0.7858 | 0.7857 | 0.7855 | 0.7852 | 0.785 | 0.7848 | 0.7841
| 9 | 0.7514 | 0.7514 | 0.7514 | 0.7513 | 0.7511 | 0.7508 | 0.7503 | 0.7496 | 0.7486 | 0.7472 | 0.7463 | 0.7454 | 0.7432
| 9.5 | 0.7075 | 0.7073 | 0.707 | 0.7064 | 0.7056 | 0.7044 | 0.7027 | 0.7004 | 0.6974 | 0.6938 | 0.6917 | 0.6895 | 0.6846
| 10 | 0.659 | 0.6581 | 0.6568 | 0.655 | 0.6526 | 0.6495 | 0.6455 | 0.6408 | 0.635 | 0.6286 | 0.6251 | 0.6215 | 0.6137
| 10.5 | 0.6088 | 0.6065 | 0.6033 | 0.5994 | 0.5946 | 0.5889 | 0.5822 | 0.5748 | 0.5665 | 0.5576 | 0.553 | 0.5484 | 0.5388
| 11 | 0.558 | 0.5534 | 0.5478 | 0.5414 | 0.5341 | 0.5259 | 0.5171 | 0.5078 | 0.4979 | 0.4878 | 0.4827 | 0.4776 | 0.4674
| 11.5 | 0.5068 | 0.4998 | 0.492 | 0.4834 | 0.4743 | 0.4646 | 0.4546 | 0.4444 | 0.4341 | 0.4239 | 0.4189 | 0.4139 | 0.404
| 12 | 0.4563 | 0.4474 | 0.438 | 0.4282 | 0.4182 | 0.408 | 0.3979 | 0.3879 | 0.378 | 0.3684 | 0.3637 | 0.3591 | 0.3502
| 12.5 | 0.408 | 0.398 | 0.3879 | 0.3778 | 0.3678 | 0.358 | 0.3484 | 0.339 | 0.33 | 0.3214 | 0.3172 | 0.3132 | 0.3053
| 13 | 0.3632 | 0.3531 | 0.3432 | 0.3334 | 0.324 | 0.3148 | 0.3061 | 0.2977 | 0.2897 | 0.2821 | 0.2784 | 0.2749 | 0.268
| 13.5 | 0.3231 | 0.3134 | 0.304 | 0.295 | 0.2864 | 0.2782 | 0.2704 | 0.263 | 0.2559 | 0.2492 | 0.246 | 0.2429 | 0.2369
| 14 | 0.2879 | 0.2789 | 0.2703 | 0.2621 | 0.2544 | 0.2471 | 0.2402 | 0.2336 | 0.2274 | 0.2216 | 0.2188 | 0.216 | 0.2108
| 14.5 | 0.2573 | 0.2491 | 0.2414 | 0.2341 | 0.2272 | 0.2207 | 0.2146 | 0.2088 | 0.2033 | 0.1982 | 0.1957 | 0.1933 | 0.1886
| 15 | 0.2308 | 0.2235 | 0.2165 | 0.21 | 0.2039 | 0.1981 | 0.1927 | 0.1876 | 0.1827 | 0.1782 | 0.176 | 0.1738 | 0.1697
| 15.5 | 0.208 | 0.2014 | 0.1952 | 0.1894 | 0.1839 | 0.1788 | 0.1739 | 0.1693 | 0.165 | 0.1609 | 0.159 | 0.1571 | 0.1534
| 16 | 0.1882 | 0.1822 | 0.1767 | 0.1715 | 0.1666 | 0.162 | 0.1576 | 0.1535 | 0.1497 | 0.146 | 0.1443 | 0.1425 | 0.1392
| 16.5 | 0.1709 | 0.1656 | 0.1606 | 0.1559 | 0.1515 | 0.1474 | 0.1435 | 0.1398 | 0.1363 | 0.133 | 0.1314 | 0.1299 | 0.1269
| 17 | 0.1559 | 0.151 | 0.1465 | 0.1423 | 0.1383 | 0.1346 | 0.131 | 0.1277 | 0.1245 | 0.1216 | 0.1201 | 0.1187 | 0.116
| 17.5 | 0.1426 | 0.1382 | 0.1341 | 0.1303 | 0.1267 | 0.1233 | 0.1201 | 0.1171 | 0.1142 | 0.1115 | 0.1102 | 0.1089 | 0.1064
| 18 | 0.1309 | 0.1269 | 0.1232 | 0.1197 | 0.1164 | 0.1133 | 0.1104 | 0.1076 | 0.105 | 0.1025 | 0.1013 | 0.1002 | 0.0979
| 18.5 | 0.1205 | 0.1168 | 0.1134 | 0.1102 | 0.1072 | 0.1044 | 0.1017 | 0.0992 | 0.0968 | 0.0946 | 0.0935 | 0.0924 | 0.0904
| 19 | 0.1111 | 0.1078 | 0.1047 | 0.1018 | 0.099 | 0.0964 | 0.094 | 0.0917 | 0.0895 | 0.0874 | 0.0864 | 0.0854 | 0.0835
| 19.5 | 0.1027 | 0.0997 | 0.0968 | 0.0941 | 0.0916 | 0.0892 | 0.087 | 0.0848 | 0.0828 | 0.0809 | 0.08 | 0.0791 | 0.0774
| 20 | 0.095 | 0.0922 | 0.0896 | 0.0871 | 0.0848 | 0.0826 | 0.0805 | 0.0786 | 0.0767 | 0.075 | 0.0741 | 0.0733 | 0.0717
| 20.5 | 0.0879 | 0.0853 | 0.0829 | 0.0807 | 0.0785 | 0.0765 | 0.0746 | 0.0728 | 0.0711 | 0.0695 | 0.0687 | 0.068 | 0.0665
| 21 | 0.0813 | 0.079 | 0.0768 | 0.0747 | 0.0727 | 0.0709 | 0.0691 | 0.0675 | 0.0659 | 0.0644 | 0.0637 | 0.063 | 0.0617
| 21.5 | 0.0752 | 0.0731 | 0.071 | 0.0691 | 0.0673 | 0.0656 | 0.064 | 0.0625 | 0.061 | 0.0597 | 0.059 | 0.0584 | 0.0571
| 22 | 0.0696 | 0.0676 | 0.0657 | 0.0639 | 0.0623 | 0.0607 | 0.0592 | 0.0578 | 0.0565 | 0.0553 | 0.0547 | 0.0541 | 0.0529
| 22.5 | 0.0643 | 0.0625 | 0.0608 | 0.0592 | 0.0576 | 0.0562 | 0.0549 | 0.0536 | 0.0524 | 0.0512 | 0.0507 | 0.0501 | 0.0491
| 23 | 0.0596 | 0.0579 | 0.0563 | 0.0548 | 0.0534 | 0.0521 | 0.0508 | 0.0497 | 0.0485 | 0.0475 | 0.047 | 0.0465 | 0.0455
| 23.5 | 0.0553 | 0.0537 | 0.0522 | 0.0509 | 0.0496 | 0.0484 | 0.0472 | 0.0461 | 0.0451 | 0.0441 | 0.0436 | 0.0432 | 0.0423
| 24 | 0.0514 | 0.0499 | 0.0486 | 0.0473 | 0.0461 | 0.045 | 0.0439 | 0.0429 | 0.042 | 0.0411 | 0.0406 | 0.0402 | 0.0394
| 24.5 | 0.0479 | 0.0466 | 0.0453 | 0.0441 | 0.043 | 0.042 | 0.041 | 0.0401 | 0.0392 | 0.0383 | 0.0379 | 0.0376 | 0.0368
| 25 | 0.0449 | 0.0436 | 0.0425 | 0.0414 | 0.0403 | 0.0394 | 0.0384 | 0.0376 | 0.0367 | 0.036 | 0.0356 | 0.0352 | 0.0345
| 25.5 | 0.0421 | 0.041 | 0.0399 | 0.0389 | 0.0379 | 0.037 | 0.0361 | 0.0353 | 0.0345 | 0.0338 | 0.0335 | 0.0331 | 0.0325
| 26 | 0.0397 | 0.0386 | 0.0376 | 0.0366 | 0.0357 | 0.0348 | 0.034 | 0.0333 | 0.0326 | 0.0319 | 0.0315 | 0.0312 | 0.0306
| 26.5 | 0.0375 | 0.0365 | 0.0355 | 0.0346 | 0.0338 | 0.033 | 0.0322 | 0.0315 | 0.0308 | 0.0302 | 0.0299 | 0.0296 | 0.029
| 27 | 0.0356 | 0.0346 | 0.0337 | 0.0329 | 0.032 | 0.0313 | 0.0306 | 0.0299 | 0.0292 | 0.0286 | 0.0283 | 0.0281 | 0.0275