## Sheet1
PROPERTIES
General
Name | Gamesa SG 5.0-145 -MOD 5 MW
Manufacturer | Gamesa
Hub Height | 91 | 95.5 | 97.5 | 127.5
Power
Rated Power | 5000
Peak Power | 5000
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 145
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 27
Restart Wind Speed | 24
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -30
Low Temperature Restart | -20
High Temperature Shutdown | 50
High Temperature Restart | 45
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | II
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 8.5
Vref | 42.5
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.24 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 41 | 44 | 46 | 49 | 52 | 54 | 56 | 57 | 60
| 4 | 200 | 207 | 215 | 222 | 230 | 237 | 241 | 245 | 252
| 5 | 471 | 486 | 502 | 517 | 532 | 547 | 555 | 563 | 578
| 6 | 864 | 891 | 917 | 943 | 969 | 996 | 1009 | 1022 | 1048
| 7 | 1409 | 1451 | 1492 | 1534 | 1576 | 1617 | 1638 | 1659 | 1700
| 8 | 2123 | 2185 | 2246 | 2308 | 2370 | 2431 | 2462 | 2493 | 2554
| 9 | 2961 | 3046 | 3130 | 3214 | 3297 | 3380 | 3421 | 3461 | 3541
| 10 | 3799 | 3898 | 3994 | 4085 | 4173 | 4255 | 4294 | 4332 | 4403
| 11 | 4484 | 4565 | 4638 | 4702 | 4759 | 4808 | 4829 | 4848 | 4881
| 12 | 4882 | 4918 | 4942 | 4958 | 4969 | 4975 | 4978 | 4980 | 4984
| 13 | 4982 | 4986 | 4989 | 4991 | 4993 | 4994 | 4995 | 4995 | 4996
| 14 | 4995 | 4996 | 4997 | 4998 | 4998 | 4999 | 4999 | 4999 | 4999
| 15 | 4999 | 4999 | 4999 | 4999 | 5000 | 5000 | 5000 | 5000 | 5000
| 16 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
| 17 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
| 18 | 4999 | 4999 | 4999 | 4999 | 4999 | 4999 | 4999 | 4999 | 4999
| 19 | 4990 | 4990 | 4990 | 4990 | 4990 | 4990 | 4990 | 4990 | 4990
| 20 | 4956 | 4956 | 4956 | 4956 | 4956 | 4956 | 4956 | 4956 | 4956
| 21 | 4869 | 4869 | 4869 | 4869 | 4869 | 4869 | 4869 | 4869 | 4869
| 22 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720
| 23 | 4531 | 4531 | 4531 | 4531 | 4531 | 4531 | 4531 | 4531 | 4531
| 24 | 4338 | 4338 | 4338 | 4337 | 4338 | 4338 | 4338 | 4338 | 4338
| 25 | 4168 | 4169 | 4168 | 4168 | 4168 | 4168 | 4169 | 4168 | 4168
| 26 | 4031 | 4031 | 4031 | 4031 | 4031 | 4031 | 4031 | 4031 | 4031
| 27 | 3930 | 3930 | 3930 | 3930 | 3930 | 3930 | 3930 | 3930 | 3930

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.24 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948 | 0.8948
| 4 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438 | 0.8438
| 5 | 0.8194 | 0.8197 | 0.8199 | 0.8202 | 0.8204 | 0.8206 | 0.8207 | 0.8207 | 0.8209
| 6 | 0.8176 | 0.8178 | 0.818 | 0.8181 | 0.8183 | 0.8184 | 0.8185 | 0.8185 | 0.8186
| 7 | 0.8189 | 0.8189 | 0.819 | 0.8191 | 0.8191 | 0.8192 | 0.8192 | 0.8192 | 0.8193
| 8 | 0.8074 | 0.8074 | 0.8075 | 0.8075 | 0.8075 | 0.8075 | 0.8075 | 0.8075 | 0.8075
| 9 | 0.7513 | 0.7512 | 0.751 | 0.7506 | 0.7501 | 0.7493 | 0.7488 | 0.7482 | 0.7468
| 10 | 0.6559 | 0.6538 | 0.6512 | 0.6478 | 0.6437 | 0.6387 | 0.636 | 0.633 | 0.6266
| 11 | 0.5442 | 0.5376 | 0.5301 | 0.522 | 0.5134 | 0.5041 | 0.4994 | 0.4946 | 0.4849
| 12 | 0.4324 | 0.4228 | 0.4131 | 0.4034 | 0.3937 | 0.3841 | 0.3794 | 0.3748 | 0.3657
| 13 | 0.3375 | 0.3283 | 0.3194 | 0.3108 | 0.3026 | 0.2947 | 0.2909 | 0.2871 | 0.28
| 14 | 0.2655 | 0.2579 | 0.2507 | 0.2439 | 0.2374 | 0.2313 | 0.2283 | 0.2255 | 0.2199
| 15 | 0.2127 | 0.2067 | 0.201 | 0.1956 | 0.1906 | 0.1857 | 0.1834 | 0.1812 | 0.1769
| 16 | 0.1736 | 0.1688 | 0.1643 | 0.16 | 0.1559 | 0.1521 | 0.1502 | 0.1484 | 0.145
| 17 | 0.1441 | 0.1401 | 0.1364 | 0.1329 | 0.1296 | 0.1265 | 0.125 | 0.1235 | 0.1207
| 18 | 0.1212 | 0.1179 | 0.1148 | 0.112 | 0.1092 | 0.1066 | 0.1054 | 0.1042 | 0.1018
| 19 | 0.103 | 0.1003 | 0.0977 | 0.0953 | 0.093 | 0.0908 | 0.0898 | 0.0887 | 0.0868
| 20 | 0.0881 | 0.0858 | 0.0836 | 0.0816 | 0.0796 | 0.0778 | 0.0769 | 0.0761 | 0.0744
| 21 | 0.0753 | 0.0734 | 0.0716 | 0.0699 | 0.0682 | 0.0667 | 0.0659 | 0.0652 | 0.0638
| 22 | 0.0643 | 0.0626 | 0.0611 | 0.0597 | 0.0583 | 0.057 | 0.0564 | 0.0558 | 0.0546
| 23 | 0.0548 | 0.0535 | 0.0522 | 0.051 | 0.0498 | 0.0487 | 0.0482 | 0.0477 | 0.0467
| 24 | 0.0471 | 0.046 | 0.0449 | 0.0439 | 0.0429 | 0.042 | 0.0415 | 0.0411 | 0.0402
| 25 | 0.041 | 0.04 | 0.0391 | 0.0382 | 0.0374 | 0.0366 | 0.0362 | 0.0358 | 0.0351
| 26 | 0.0362 | 0.0353 | 0.0345 | 0.0337 | 0.033 | 0.0323 | 0.0319 | 0.0316 | 0.031
| 27 | 0.0324 | 0.0316 | 0.0309 | 0.0302 | 0.0295 | 0.0289 | 0.0286 | 0.0283 | 0.0278