## Sheet1
PROPERTIES
General
Name | Gamesa SG 6.0-155 -MOD 6,1 MW
Manufacturer | Gamesa
Hub Height | 90 | 102.5 | 107.5 | 113.5 | 120.5 | 122.5 | 165
Power
Rated Power | 6100
Peak Power | 6100
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 155
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 27
Restart Wind Speed | 24
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -30
Low Temperature Restart | -20
High Temperature Shutdown | 50
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | II
Turbine SubClass | A/B
Values
Certification | IEC 3rd Edition
Vave | 8.5
Vref | 42.5
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.225
Wind Speed (m/s) | 0 | 0
| 0.5 | 0
| 1 | 0
| 1.5 | 0
| 2 | 0
| 2.5 | 0
| 3 | 50
| 3.5 | 132
| 4 | 258
| 4.5 | 421
| 5 | 619
| 5.5 | 854
| 6 | 1134
| 6.5 | 1463
| 7 | 1846
| 7.5 | 2286
| 8 | 2780
| 8.5 | 3314
| 9 | 3866
| 9.5 | 4406
| 10 | 4897
| 10.5 | 5305
| 11 | 5611
| 11.5 | 5819
| 12 | 5947
| 12.5 | 6021
| 13 | 6061
| 13.5 | 6081
| 14 | 6091
| 14.5 | 6096
| 15 | 6098
| 15.5 | 6099
| 16 | 6100
| 16.5 | 6100
| 17 | 6100
| 17.5 | 6100
| 18 | 6100
| 18.5 | 6099
| 19 | 6097
| 19.5 | 6093
| 20 | 6085
| 20.5 | 6071
| 21 | 6049
| 21.5 | 6016
| 22 | 5973
| 22.5 | 5917
| 23 | 5850
| 23.5 | 5774
| 24 | 5692
| 24.5 | 5605
| 25 | 5519
| 25.5 | 5433
| 26 | 5353
| 26.5 | 5280
| 27 | 5215

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
1.225
Wind Speed (m/s) | 0 | 0
| 0.5 | 0
| 1 | 0
| 1.5 | 0
| 2 | 0
| 2.5 | 0
| 3 | 0.894
| 3.5 | 0.876
| 4 | 0.856
| 4.5 | 0.838
| 5 | 0.825
| 5.5 | 0.82
| 6 | 0.821
| 6.5 | 0.824
| 7 | 0.825
| 7.5 | 0.823
| 8 | 0.812
| 8.5 | 0.787
| 9 | 0.749
| 9.5 | 0.701
| 10 | 0.646
| 10.5 | 0.586
| 11 | 0.525
| 11.5 | 0.464
| 12 | 0.408
| 12.5 | 0.358
| 13 | 0.315
| 13.5 | 0.279
| 14 | 0.248
| 14.5 | 0.222
| 15 | 0.199
| 15.5 | 0.18
| 16 | 0.163
| 16.5 | 0.148
| 17 | 0.136
| 17.5 | 0.124
| 18 | 0.115
| 18.5 | 0.106
| 19 | 0.098
| 19.5 | 0.091
| 20 | 0.084
| 20.5 | 0.078
| 21 | 0.073
| 21.5 | 0.068
| 22 | 0.063
| 22.5 | 0.059
| 23 | 0.055
| 23.5 | 0.051
| 24 | 0.048
| 24.5 | 0.045
| 25 | 0.042
| 25.5 | 0.039
| 26 | 0.037
| 26.5 | 0.035
| 27 | 0.033