## Sheet1
PROPERTIES
General
Name | Gamesa SG 6.0-155 -MOD 6,2 MW
Manufacturer | Gamesa
Hub Height | 90 | 102.5 | 107.5 | 113.5 | 120.5 | 122.5 | 165
Power
Rated Power | 6200
Peak Power | 6200
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 155
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 27
Restart Wind Speed | 24
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -30
Low Temperature Restart | -20
High Temperature Shutdown | 50
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | II
Turbine SubClass | A/B
Values
Certification | IEC 3rd Edition
Vave | 8.5
Vref | 42.5
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.225
Wind Speed (m/s) | 0 | 0
| 0.5 | 0
| 1 | 0
| 1.5 | 0
| 2 | 0
| 2.5 | 0
| 3 | 49
| 3.5 | 130
| 4 | 257
| 4.5 | 420
| 5 | 618
| 5.5 | 853
| 6 | 1132
| 6.5 | 1462
| 7 | 1845
| 7.5 | 2285
| 8 | 2779
| 8.5 | 3314
| 9 | 3867
| 9.5 | 4410
| 10 | 4910
| 10.5 | 5334
| 11 | 5658
| 11.5 | 5883
| 12 | 6025
| 12.5 | 6108
| 13 | 6153
| 13.5 | 6177
| 14 | 6189
| 14.5 | 6195
| 15 | 6198
| 15.5 | 6199
| 16 | 6200
| 16.5 | 6200
| 17 | 6200
| 17.5 | 6200
| 18 | 6200
| 18.5 | 6199
| 19 | 6196
| 19.5 | 6191
| 20 | 6181
| 20.5 | 6165
| 21 | 6138
| 21.5 | 6101
| 22 | 6050
| 22.5 | 5987
| 23 | 5912
| 23.5 | 5828
| 24 | 5736
| 24.5 | 5642
| 25 | 5549
| 25.5 | 5457
| 26 | 5372
| 26.5 | 5294
| 27 | 5226

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
1.225
Wind Speed (m/s) | 0 | 0
| 0.5 | 0
| 1 | 0
| 1.5 | 0
| 2 | 0
| 2.5 | 0
| 3 | 0.894
| 3.5 | 0.876
| 4 | 0.856
| 4.5 | 0.838
| 5 | 0.825
| 5.5 | 0.82
| 6 | 0.821
| 6.5 | 0.824
| 7 | 0.825
| 7.5 | 0.823
| 8 | 0.812
| 8.5 | 0.787
| 9 | 0.749
| 9.5 | 0.702
| 10 | 0.648
| 10.5 | 0.59
| 11 | 0.529
| 11.5 | 0.47
| 12 | 0.414
| 12.5 | 0.364
| 13 | 0.321
| 13.5 | 0.284
| 14 | 0.252
| 14.5 | 0.225
| 15 | 0.202
| 15.5 | 0.183
| 16 | 0.166
| 16.5 | 0.151
| 17 | 0.138
| 17.5 | 0.126
| 18 | 0.116
| 18.5 | 0.107
| 19 | 0.099
| 19.5 | 0.092
| 20 | 0.085
| 20.5 | 0.079
| 21 | 0.074
| 21.5 | 0.069
| 22 | 0.064
| 22.5 | 0.06
| 23 | 0.056
| 23.5 | 0.052
| 24 | 0.048
| 24.5 | 0.045
| 25 | 0.042
| 25.5 | 0.039
| 26 | 0.037
| 26.5 | 0.035
| 27 | 0.033