## Sheet1
PROPERTIES
General
Name | Gamesa SG 6.0-155 -MOD 6,5 MW
Manufacturer | Gamesa
Hub Height | 90 | 102.5 | 107.5 | 113.5 | 120.5 | 122.5 | 165
Power
Rated Power | 6500
Peak Power | 6500
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 155
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 27
Restart Wind Speed | 24
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -30
Low Temperature Restart | -20
High Temperature Shutdown | 50
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | II
Turbine SubClass | A/B
Values
Certification | IEC 3rd Edition
Vave | 8.5
Vref | 42.5
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.225
Wind Speed (m/s) | 0 | 0
| 0.5 | 0
| 1 | 0
| 1.5 | 0
| 2 | 0
| 2.5 | 0
| 3 | 47
| 3.5 | 127
| 4 | 253
| 4.5 | 416
| 5 | 614
| 5.5 | 849
| 6 | 1129
| 6.5 | 1458
| 7 | 1842
| 7.5 | 2282
| 8 | 2776
| 8.5 | 3312
| 9 | 3868
| 9.5 | 4420
| 10 | 4941
| 10.5 | 5403
| 11 | 5778
| 11.5 | 6055
| 12 | 6242
| 12.5 | 6358
| 13 | 6425
| 13.5 | 6462
| 14 | 6481
| 14.5 | 6491
| 15 | 6496
| 15.5 | 6498
| 16 | 6499
| 16.5 | 6500
| 17 | 6500
| 17.5 | 6500
| 18 | 6499
| 18.5 | 6497
| 19 | 6493
| 19.5 | 6484
| 20 | 6468
| 20.5 | 6442
| 21 | 6401
| 21.5 | 6345
| 22 | 6273
| 22.5 | 6185
| 23 | 6084
| 23.5 | 5974
| 24 | 5858
| 24.5 | 5742
| 25 | 5629
| 25.5 | 5520
| 26 | 5420
| 26.5 | 5331
| 27 | 5255

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
1.225
Wind Speed (m/s) | 0 | 0
| 0.5 | 0
| 1 | 0
| 1.5 | 0
| 2 | 0
| 2.5 | 0
| 3 | 0.894
| 3.5 | 0.876
| 4 | 0.856
| 4.5 | 0.838
| 5 | 0.825
| 5.5 | 0.82
| 6 | 0.821
| 6.5 | 0.824
| 7 | 0.825
| 7.5 | 0.823
| 8 | 0.812
| 8.5 | 0.787
| 9 | 0.75
| 9.5 | 0.703
| 10 | 0.652
| 10.5 | 0.598
| 11 | 0.542
| 11.5 | 0.485
| 12 | 0.431
| 12.5 | 0.381
| 13 | 0.336
| 13.5 | 0.298
| 14 | 0.265
| 14.5 | 0.237
| 15 | 0.213
| 15.5 | 0.192
| 16 | 0.174
| 16.5 | 0.158
| 17 | 0.144
| 17.5 | 0.132
| 18 | 0.122
| 18.5 | 0.112
| 19 | 0.104
| 19.5 | 0.096
| 20 | 0.089
| 20.5 | 0.083
| 21 | 0.077
| 21.5 | 0.071
| 22 | 0.066
| 22.5 | 0.062
| 23 | 0.057
| 23.5 | 0.053
| 24 | 0.049
| 24.5 | 0.046
| 25 | 0.043
| 25.5 | 0.04
| 26 | 0.037
| 26.5 | 0.035
| 27 | 0.033