## Sheet1
PROPERTIES
General
Name | Gamesa SG 6.6-170 -MOD 6,0 MW_v2
Manufacturer | Gamesa
Hub Height | 100 | 115 | 135 | 145 | 155 | 165
Power
Rated Power | 6000
Peak Power | 6000
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 170
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 25
Restart Wind Speed | 22
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -30
Low Temperature Restart | -20
High Temperature Shutdown | 50
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 7.38
Vref | 42.5
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.03 | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.24 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 72 | 75 | 77 | 80 | 82 | 85 | 88 | 89 | 90 | 93
| 3.5 | 139 | 145 | 151 | 157 | 163 | 169 | 175 | 178 | 181 | 187
| 4 | 261 | 272 | 282 | 292 | 302 | 312 | 323 | 328 | 333 | 343
| 4.5 | 424 | 439 | 454 | 470 | 485 | 500 | 515 | 522 | 530 | 545
| 5 | 624 | 645 | 665 | 686 | 707 | 728 | 749 | 759 | 769 | 790
| 5.5 | 866 | 894 | 921 | 949 | 977 | 1005 | 1033 | 1046 | 1060 | 1088
| 6 | 1157 | 1194 | 1230 | 1266 | 1303 | 1339 | 1375 | 1393 | 1411 | 1448
| 6.5 | 1500 | 1547 | 1593 | 1639 | 1685 | 1732 | 1778 | 1801 | 1824 | 1870
| 7 | 1897 | 1955 | 2012 | 2070 | 2128 | 2186 | 2243 | 2272 | 2301 | 2358
| 7.5 | 2350 | 2421 | 2491 | 2562 | 2633 | 2703 | 2774 | 2809 | 2844 | 2914
| 8 | 2855 | 2940 | 3025 | 3110 | 3195 | 3279 | 3363 | 3405 | 3446 | 3529
| 8.5 | 3397 | 3497 | 3597 | 3695 | 3793 | 3889 | 3984 | 4030 | 4077 | 4167
| 9 | 3949 | 4062 | 4173 | 4281 | 4385 | 4486 | 4582 | 4628 | 4674 | 4760
| 9.5 | 4475 | 4595 | 4708 | 4815 | 4914 | 5006 | 5091 | 5130 | 5170 | 5240
| 10 | 4938 | 5054 | 5157 | 5249 | 5331 | 5404 | 5469 | 5498 | 5527 | 5576
| 10.5 | 5311 | 5410 | 5492 | 5561 | 5621 | 5671 | 5714 | 5733 | 5752 | 5782
| 11 | 5582 | 5657 | 5715 | 5762 | 5800 | 5831 | 5857 | 5867 | 5878 | 5895
| 11.5 | 5762 | 5813 | 5850 | 5878 | 5900 | 5918 | 5932 | 5938 | 5943 | 5952
| 12 | 5872 | 5903 | 5925 | 5941 | 5953 | 5962 | 5969 | 5972 | 5975 | 5979
| 12.5 | 5934 | 5952 | 5964 | 5972 | 5978 | 5983 | 5986 | 5987 | 5989 | 5991
| 13 | 5967 | 5977 | 5983 | 5987 | 5990 | 5992 | 5994 | 5995 | 5995 | 5996
| 13.5 | 5984 | 5989 | 5992 | 5994 | 5996 | 5997 | 5997 | 5998 | 5998 | 5998
| 14 | 5992 | 5995 | 5996 | 5997 | 5998 | 5999 | 5999 | 5999 | 5999 | 5999
| 14.5 | 5996 | 5998 | 5998 | 5999 | 5999 | 5999 | 6000 | 6000 | 6000 | 6000
| 15 | 5998 | 5999 | 5999 | 5999 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000
| 15.5 | 5999 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000
| 16 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000
| 16.5 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000
| 17 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000
| 17.5 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000
| 18 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000
| 18.5 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000
| 19 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000
| 19.5 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000
| 20 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000
| 20.5 | 5880 | 5880 | 5880 | 5880 | 5880 | 5880 | 5880 | 5880 | 5880 | 5880
| 21 | 5760 | 5760 | 5760 | 5760 | 5760 | 5760 | 5760 | 5760 | 5760 | 5760
| 21.5 | 5640 | 5640 | 5640 | 5640 | 5640 | 5640 | 5640 | 5640 | 5640 | 5640
| 22 | 5520 | 5520 | 5520 | 5520 | 5520 | 5520 | 5520 | 5520 | 5520 | 5520
| 22.5 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400
| 23 | 5280 | 5280 | 5280 | 5280 | 5280 | 5280 | 5280 | 5280 | 5280 | 5280
| 23.5 | 5160 | 5160 | 5160 | 5160 | 5160 | 5160 | 5160 | 5160 | 5160 | 5160
| 24 | 5040 | 5040 | 5040 | 5040 | 5040 | 5040 | 5040 | 5040 | 5040 | 5040
| 24.5 | 4920 | 4920 | 4920 | 4920 | 4920 | 4920 | 4920 | 4920 | 4920 | 4920
| 25 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.03 | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.24 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953
| 3.5 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
| 4 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847
| 4.5 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828
| 5 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824
| 5.5 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828
| 6 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833
| 6.5 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836
| 7 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837
| 7.5 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835
| 8 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.824 | 0.824
| 8.5 | 0.804 | 0.804 | 0.803 | 0.803 | 0.803 | 0.802 | 0.801 | 0.8 | 0.799 | 0.797
| 9 | 0.767 | 0.767 | 0.766 | 0.764 | 0.762 | 0.76 | 0.756 | 0.754 | 0.752 | 0.746
| 9.5 | 0.716 | 0.714 | 0.712 | 0.708 | 0.703 | 0.698 | 0.691 | 0.687 | 0.683 | 0.674
| 10 | 0.654 | 0.651 | 0.645 | 0.639 | 0.631 | 0.622 | 0.612 | 0.607 | 0.602 | 0.59
| 10.5 | 0.587 | 0.581 | 0.573 | 0.564 | 0.553 | 0.543 | 0.531 | 0.525 | 0.52 | 0.508
| 11 | 0.52 | 0.511 | 0.501 | 0.491 | 0.48 | 0.468 | 0.457 | 0.451 | 0.446 | 0.435
| 11.5 | 0.456 | 0.447 | 0.436 | 0.425 | 0.414 | 0.403 | 0.393 | 0.388 | 0.383 | 0.373
| 12 | 0.399 | 0.389 | 0.379 | 0.369 | 0.359 | 0.349 | 0.34 | 0.335 | 0.331 | 0.322
| 12.5 | 0.35 | 0.34 | 0.331 | 0.321 | 0.313 | 0.304 | 0.296 | 0.292 | 0.288 | 0.281
| 13 | 0.308 | 0.299 | 0.29 | 0.282 | 0.274 | 0.267 | 0.26 | 0.256 | 0.253 | 0.247
| 13.5 | 0.272 | 0.264 | 0.256 | 0.249 | 0.242 | 0.236 | 0.23 | 0.227 | 0.224 | 0.219
| 14 | 0.242 | 0.235 | 0.228 | 0.222 | 0.216 | 0.21 | 0.205 | 0.202 | 0.2 | 0.195
| 14.5 | 0.216 | 0.21 | 0.204 | 0.198 | 0.193 | 0.188 | 0.183 | 0.181 | 0.179 | 0.175
| 15 | 0.194 | 0.189 | 0.183 | 0.179 | 0.174 | 0.169 | 0.165 | 0.163 | 0.161 | 0.158
| 15.5 | 0.176 | 0.171 | 0.166 | 0.161 | 0.157 | 0.153 | 0.15 | 0.148 | 0.146 | 0.143
| 16 | 0.159 | 0.155 | 0.151 | 0.147 | 0.143 | 0.139 | 0.136 | 0.135 | 0.133 | 0.13
| 16.5 | 0.145 | 0.141 | 0.138 | 0.134 | 0.131 | 0.127 | 0.124 | 0.123 | 0.122 | 0.119
| 17 | 0.133 | 0.13 | 0.126 | 0.123 | 0.12 | 0.117 | 0.114 | 0.113 | 0.112 | 0.109
| 17.5 | 0.123 | 0.12 | 0.117 | 0.114 | 0.111 | 0.108 | 0.106 | 0.104 | 0.103 | 0.101
| 18 | 0.114 | 0.111 | 0.108 | 0.105 | 0.103 | 0.1 | 0.098 | 0.097 | 0.096 | 0.094
| 18.5 | 0.106 | 0.103 | 0.101 | 0.098 | 0.096 | 0.094 | 0.091 | 0.09 | 0.089 | 0.087
| 19 | 0.1 | 0.097 | 0.094 | 0.092 | 0.09 | 0.088 | 0.086 | 0.085 | 0.084 | 0.082
| 19.5 | 0.093 | 0.091 | 0.089 | 0.086 | 0.084 | 0.082 | 0.081 | 0.08 | 0.079 | 0.077
| 20 | 0.088 | 0.086 | 0.084 | 0.081 | 0.08 | 0.078 | 0.076 | 0.075 | 0.074 | 0.073
| 20.5 | 0.074 | 0.073 | 0.071 | 0.069 | 0.067 | 0.066 | 0.064 | 0.064 | 0.063 | 0.062
| 21 | 0.068 | 0.066 | 0.065 | 0.063 | 0.062 | 0.06 | 0.059 | 0.059 | 0.058 | 0.057
| 21.5 | 0.062 | 0.061 | 0.059 | 0.058 | 0.057 | 0.055 | 0.054 | 0.054 | 0.053 | 0.052
| 22 | 0.057 | 0.056 | 0.055 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.049 | 0.048
| 22.5 | 0.053 | 0.052 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.046 | 0.045 | 0.044
| 23 | 0.049 | 0.048 | 0.046 | 0.045 | 0.044 | 0.043 | 0.043 | 0.042 | 0.042 | 0.041
| 23.5 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.038
| 24 | 0.042 | 0.041 | 0.04 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.036 | 0.035
| 24.5 | 0.039 | 0.038 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.034 | 0.033 | 0.033
| 25 | 0.036 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.031 | 0.031 | 0.031 | 0.03