## Sheet1
PROPERTIES
General
Name | Gamesa SG 6.6-170 -MOD 6,2 MW_v2
Manufacturer | Gamesa
Hub Height | 100 | 115 | 135 | 145 | 155 | 165
Power
Rated Power | 6200
Peak Power | 6200
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 170
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 25
Restart Wind Speed | 22
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -30
Low Temperature Restart | -20
High Temperature Shutdown | 50
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 7.38
Vref | 42.5
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.03 | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.24 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 72 | 75 | 77 | 80 | 82 | 85 | 88 | 89 | 90 | 93
| 3.5 | 139 | 145 | 151 | 157 | 163 | 169 | 175 | 178 | 181 | 187
| 4 | 261 | 272 | 282 | 292 | 302 | 312 | 323 | 328 | 333 | 343
| 4.5 | 424 | 439 | 454 | 470 | 485 | 500 | 515 | 522 | 530 | 545
| 5 | 624 | 645 | 665 | 686 | 707 | 728 | 749 | 759 | 769 | 790
| 5.5 | 866 | 894 | 921 | 949 | 977 | 1005 | 1033 | 1046 | 1060 | 1088
| 6 | 1157 | 1194 | 1230 | 1266 | 1303 | 1339 | 1375 | 1393 | 1411 | 1448
| 6.5 | 1500 | 1547 | 1593 | 1639 | 1685 | 1732 | 1778 | 1801 | 1824 | 1870
| 7 | 1897 | 1955 | 2012 | 2070 | 2128 | 2186 | 2243 | 2272 | 2301 | 2358
| 7.5 | 2350 | 2421 | 2491 | 2562 | 2633 | 2703 | 2774 | 2809 | 2844 | 2914
| 8 | 2855 | 2940 | 3025 | 3110 | 3195 | 3280 | 3364 | 3406 | 3448 | 3531
| 8.5 | 3397 | 3498 | 3598 | 3697 | 3796 | 3894 | 3990 | 4038 | 4085 | 4178
| 9 | 3950 | 4065 | 4178 | 4290 | 4398 | 4503 | 4605 | 4654 | 4702 | 4795
| 9.5 | 4481 | 4606 | 4727 | 4842 | 4950 | 5051 | 5145 | 5190 | 5232 | 5312
| 10 | 4958 | 5085 | 5202 | 5308 | 5402 | 5487 | 5562 | 5597 | 5629 | 5689
| 10.5 | 5356 | 5472 | 5573 | 5658 | 5731 | 5793 | 5845 | 5869 | 5890 | 5929
| 11 | 5662 | 5756 | 5833 | 5894 | 5943 | 5983 | 6016 | 6031 | 6043 | 6066
| 11.5 | 5877 | 5946 | 5998 | 6037 | 6068 | 6091 | 6110 | 6118 | 6125 | 6137
| 12 | 6017 | 6062 | 6095 | 6118 | 6135 | 6148 | 6158 | 6162 | 6165 | 6171
| 12.5 | 6101 | 6128 | 6147 | 6160 | 6169 | 6176 | 6181 | 6183 | 6185 | 6187
| 13 | 6148 | 6164 | 6175 | 6181 | 6186 | 6189 | 6191 | 6192 | 6193 | 6195
| 13.5 | 6174 | 6183 | 6188 | 6191 | 6194 | 6195 | 6196 | 6197 | 6197 | 6198
| 14 | 6187 | 6192 | 6194 | 6196 | 6197 | 6198 | 6198 | 6199 | 6199 | 6199
| 14.5 | 6194 | 6196 | 6197 | 6198 | 6199 | 6199 | 6199 | 6199 | 6199 | 6200
| 15 | 6197 | 6198 | 6199 | 6199 | 6199 | 6200 | 6200 | 6200 | 6200 | 6200
| 15.5 | 6199 | 6199 | 6199 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200
| 16 | 6199 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200
| 16.5 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200
| 17 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200
| 17.5 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200
| 18 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200
| 18.5 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200
| 19 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200
| 19.5 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200
| 20 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200
| 20.5 | 6076 | 6076 | 6076 | 6076 | 6076 | 6076 | 6076 | 6076 | 6076 | 6076
| 21 | 5952 | 5952 | 5952 | 5952 | 5952 | 5952 | 5952 | 5952 | 5952 | 5952
| 21.5 | 5828 | 5828 | 5828 | 5828 | 5828 | 5828 | 5828 | 5828 | 5828 | 5828
| 22 | 5704 | 5704 | 5704 | 5704 | 5704 | 5704 | 5704 | 5704 | 5704 | 5704
| 22.5 | 5580 | 5580 | 5580 | 5580 | 5580 | 5580 | 5580 | 5580 | 5580 | 5580
| 23 | 5456 | 5456 | 5456 | 5456 | 5456 | 5456 | 5456 | 5456 | 5456 | 5456
| 23.5 | 5332 | 5332 | 5332 | 5332 | 5332 | 5332 | 5332 | 5332 | 5332 | 5332
| 24 | 5208 | 5208 | 5208 | 5208 | 5208 | 5208 | 5208 | 5208 | 5208 | 5208
| 24.5 | 5084 | 5084 | 5084 | 5084 | 5084 | 5084 | 5084 | 5084 | 5084 | 5084
| 25 | 4960 | 4960 | 4960 | 4960 | 4960 | 4960 | 4960 | 4960 | 4960 | 4960

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.03 | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.24 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953
| 3.5 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
| 4 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847
| 4.5 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828
| 5 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824
| 5.5 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828
| 6 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833
| 6.5 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836
| 7 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837
| 7.5 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835
| 8 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825
| 8.5 | 0.804 | 0.804 | 0.804 | 0.804 | 0.803 | 0.803 | 0.802 | 0.802 | 0.801 | 0.8
| 9 | 0.767 | 0.767 | 0.767 | 0.766 | 0.765 | 0.763 | 0.761 | 0.759 | 0.757 | 0.753
| 9.5 | 0.717 | 0.716 | 0.715 | 0.712 | 0.709 | 0.705 | 0.699 | 0.696 | 0.693 | 0.686
| 10 | 0.657 | 0.654 | 0.651 | 0.646 | 0.64 | 0.633 | 0.625 | 0.62 | 0.615 | 0.605
| 10.5 | 0.592 | 0.588 | 0.582 | 0.575 | 0.566 | 0.556 | 0.546 | 0.541 | 0.535 | 0.524
| 11 | 0.527 | 0.521 | 0.513 | 0.503 | 0.493 | 0.483 | 0.472 | 0.466 | 0.461 | 0.45
| 11.5 | 0.466 | 0.458 | 0.448 | 0.438 | 0.428 | 0.417 | 0.407 | 0.402 | 0.396 | 0.386
| 12 | 0.41 | 0.401 | 0.391 | 0.381 | 0.371 | 0.361 | 0.352 | 0.347 | 0.343 | 0.334
| 12.5 | 0.361 | 0.351 | 0.342 | 0.333 | 0.324 | 0.315 | 0.307 | 0.303 | 0.299 | 0.291
| 13 | 0.318 | 0.309 | 0.3 | 0.292 | 0.284 | 0.276 | 0.269 | 0.266 | 0.262 | 0.256
| 13.5 | 0.281 | 0.273 | 0.265 | 0.258 | 0.251 | 0.244 | 0.238 | 0.235 | 0.232 | 0.226
| 14 | 0.25 | 0.243 | 0.236 | 0.229 | 0.223 | 0.217 | 0.212 | 0.209 | 0.207 | 0.202
| 14.5 | 0.224 | 0.217 | 0.211 | 0.205 | 0.2 | 0.195 | 0.19 | 0.187 | 0.185 | 0.181
| 15 | 0.201 | 0.195 | 0.19 | 0.185 | 0.18 | 0.175 | 0.171 | 0.169 | 0.167 | 0.163
| 15.5 | 0.181 | 0.176 | 0.171 | 0.167 | 0.163 | 0.158 | 0.155 | 0.153 | 0.151 | 0.147
| 16 | 0.165 | 0.16 | 0.156 | 0.152 | 0.148 | 0.144 | 0.141 | 0.139 | 0.137 | 0.134
| 16.5 | 0.15 | 0.146 | 0.142 | 0.138 | 0.135 | 0.132 | 0.128 | 0.127 | 0.125 | 0.123
| 17 | 0.138 | 0.134 | 0.13 | 0.127 | 0.124 | 0.121 | 0.118 | 0.117 | 0.115 | 0.113
| 17.5 | 0.127 | 0.124 | 0.12 | 0.117 | 0.114 | 0.112 | 0.109 | 0.108 | 0.106 | 0.104
| 18 | 0.118 | 0.115 | 0.112 | 0.109 | 0.106 | 0.104 | 0.101 | 0.1 | 0.099 | 0.097
| 18.5 | 0.11 | 0.107 | 0.104 | 0.101 | 0.099 | 0.096 | 0.094 | 0.093 | 0.092 | 0.09
| 19 | 0.103 | 0.1 | 0.097 | 0.095 | 0.093 | 0.09 | 0.088 | 0.087 | 0.086 | 0.084
| 19.5 | 0.096 | 0.094 | 0.091 | 0.089 | 0.087 | 0.085 | 0.083 | 0.082 | 0.081 | 0.079
| 20 | 0.091 | 0.088 | 0.086 | 0.084 | 0.082 | 0.08 | 0.078 | 0.077 | 0.076 | 0.075
| 20.5 | 0.077 | 0.075 | 0.073 | 0.071 | 0.069 | 0.068 | 0.066 | 0.066 | 0.065 | 0.064
| 21 | 0.07 | 0.068 | 0.067 | 0.065 | 0.064 | 0.062 | 0.061 | 0.06 | 0.06 | 0.058
| 21.5 | 0.064 | 0.063 | 0.061 | 0.06 | 0.058 | 0.057 | 0.056 | 0.055 | 0.055 | 0.054
| 22 | 0.059 | 0.058 | 0.056 | 0.055 | 0.054 | 0.053 | 0.051 | 0.051 | 0.05 | 0.049
| 22.5 | 0.054 | 0.053 | 0.052 | 0.051 | 0.049 | 0.048 | 0.047 | 0.047 | 0.046 | 0.046
| 23 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.043 | 0.042
| 23.5 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.04 | 0.039
| 24 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.038 | 0.037 | 0.037 | 0.037 | 0.036
| 24.5 | 0.04 | 0.039 | 0.038 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.034 | 0.033
| 25 | 0.037 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032 | 0.032 | 0.032 | 0.031