## Sheet1
PROPERTIES
General
Name | Gamesa SG 6.6-170 -MOD 6,3 MW_v2
Manufacturer | Gamesa
Hub Height | 100 | 115 | 135 | 145 | 155 | 165
Power
Rated Power | 6300
Peak Power | 6300
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 170
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 25
Restart Wind Speed | 22
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -30
Low Temperature Restart | -20
High Temperature Shutdown | 50
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 7.38
Vref | 42.5
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.03 | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.24 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 72 | 75 | 77 | 80 | 82 | 85 | 88 | 89 | 90 | 93
| 3.5 | 139 | 145 | 151 | 157 | 163 | 169 | 175 | 178 | 181 | 187
| 4 | 261 | 272 | 282 | 292 | 302 | 312 | 323 | 328 | 333 | 343
| 4.5 | 424 | 439 | 454 | 470 | 485 | 500 | 515 | 522 | 530 | 545
| 5 | 624 | 645 | 665 | 686 | 707 | 728 | 749 | 759 | 769 | 790
| 5.5 | 866 | 894 | 921 | 949 | 977 | 1005 | 1033 | 1046 | 1060 | 1088
| 6 | 1157 | 1194 | 1230 | 1266 | 1303 | 1339 | 1375 | 1393 | 1411 | 1448
| 6.5 | 1500 | 1547 | 1593 | 1639 | 1685 | 1732 | 1778 | 1801 | 1824 | 1870
| 7 | 1897 | 1955 | 2012 | 2070 | 2128 | 2186 | 2243 | 2272 | 2301 | 2358
| 7.5 | 2350 | 2421 | 2491 | 2562 | 2633 | 2703 | 2774 | 2809 | 2844 | 2914
| 8 | 2855 | 2940 | 3025 | 3110 | 3195 | 3280 | 3364 | 3406 | 3448 | 3532
| 8.5 | 3397 | 3498 | 3598 | 3698 | 3797 | 3895 | 3992 | 4040 | 4088 | 4183
| 9 | 3950 | 4065 | 4180 | 4292 | 4403 | 4510 | 4614 | 4664 | 4714 | 4810
| 9.5 | 4482 | 4610 | 4733 | 4852 | 4964 | 5069 | 5168 | 5214 | 5259 | 5344
| 10 | 4964 | 5096 | 5219 | 5331 | 5432 | 5523 | 5604 | 5641 | 5676 | 5741
| 10.5 | 5372 | 5496 | 5605 | 5699 | 5779 | 5848 | 5906 | 5932 | 5956 | 5999
| 11 | 5692 | 5797 | 5884 | 5954 | 6010 | 6055 | 6092 | 6109 | 6123 | 6149
| 11.5 | 5924 | 6004 | 6066 | 6112 | 6148 | 6175 | 6197 | 6206 | 6214 | 6228
| 12 | 6080 | 6135 | 6175 | 6204 | 6224 | 6239 | 6251 | 6256 | 6260 | 6267
| 12.5 | 6178 | 6213 | 6236 | 6252 | 6264 | 6272 | 6277 | 6280 | 6282 | 6285
| 13 | 6235 | 6255 | 6269 | 6277 | 6283 | 6287 | 6290 | 6291 | 6292 | 6294
| 13.5 | 6266 | 6278 | 6285 | 6289 | 6292 | 6294 | 6295 | 6296 | 6296 | 6297
| 14 | 6283 | 6289 | 6293 | 6295 | 6296 | 6297 | 6298 | 6298 | 6298 | 6299
| 14.5 | 6292 | 6295 | 6297 | 6298 | 6298 | 6299 | 6299 | 6299 | 6299 | 6299
| 15 | 6296 | 6298 | 6298 | 6299 | 6299 | 6299 | 6300 | 6300 | 6300 | 6300
| 15.5 | 6298 | 6299 | 6299 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300
| 16 | 6299 | 6299 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300
| 16.5 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300
| 17 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300
| 17.5 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300
| 18 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300
| 18.5 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300
| 19 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300
| 19.5 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300
| 20 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300
| 20.5 | 6174 | 6174 | 6174 | 6174 | 6174 | 6174 | 6174 | 6174 | 6174 | 6174
| 21 | 6048 | 6048 | 6048 | 6048 | 6048 | 6048 | 6048 | 6048 | 6048 | 6048
| 21.5 | 5922 | 5922 | 5922 | 5922 | 5922 | 5922 | 5922 | 5922 | 5922 | 5922
| 22 | 5796 | 5796 | 5796 | 5796 | 5796 | 5796 | 5796 | 5796 | 5796 | 5796
| 22.5 | 5670 | 5670 | 5670 | 5670 | 5670 | 5670 | 5670 | 5670 | 5670 | 5670
| 23 | 5544 | 5544 | 5544 | 5544 | 5544 | 5544 | 5544 | 5544 | 5544 | 5544
| 23.5 | 5418 | 5418 | 5418 | 5418 | 5418 | 5418 | 5418 | 5418 | 5418 | 5418
| 24 | 5292 | 5292 | 5292 | 5292 | 5292 | 5292 | 5292 | 5292 | 5292 | 5292
| 24.5 | 5166 | 5166 | 5166 | 5166 | 5166 | 5166 | 5166 | 5166 | 5166 | 5166
| 25 | 5040 | 5040 | 5040 | 5040 | 5040 | 5040 | 5040 | 5040 | 5040 | 5040

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.03 | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.24 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953
| 3.5 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
| 4 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847
| 4.5 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828
| 5 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824
| 5.5 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828
| 6 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833
| 6.5 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836
| 7 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837
| 7.5 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835
| 8 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825
| 8.5 | 0.804 | 0.804 | 0.804 | 0.804 | 0.803 | 0.803 | 0.803 | 0.802 | 0.802 | 0.801
| 9 | 0.767 | 0.767 | 0.767 | 0.767 | 0.766 | 0.764 | 0.762 | 0.761 | 0.76 | 0.756
| 9.5 | 0.717 | 0.716 | 0.716 | 0.714 | 0.711 | 0.708 | 0.703 | 0.7 | 0.697 | 0.691
| 10 | 0.657 | 0.656 | 0.653 | 0.649 | 0.644 | 0.638 | 0.63 | 0.626 | 0.622 | 0.612
| 10.5 | 0.594 | 0.59 | 0.585 | 0.579 | 0.571 | 0.562 | 0.553 | 0.548 | 0.542 | 0.532
| 11 | 0.53 | 0.525 | 0.518 | 0.509 | 0.5 | 0.489 | 0.479 | 0.473 | 0.468 | 0.457
| 11.5 | 0.47 | 0.463 | 0.454 | 0.444 | 0.434 | 0.424 | 0.413 | 0.408 | 0.403 | 0.393
| 12 | 0.415 | 0.406 | 0.397 | 0.387 | 0.377 | 0.368 | 0.358 | 0.353 | 0.349 | 0.34
| 12.5 | 0.365 | 0.357 | 0.347 | 0.338 | 0.329 | 0.32 | 0.312 | 0.308 | 0.304 | 0.296
| 13 | 0.323 | 0.314 | 0.305 | 0.297 | 0.289 | 0.281 | 0.274 | 0.27 | 0.267 | 0.26
| 13.5 | 0.286 | 0.278 | 0.27 | 0.262 | 0.255 | 0.248 | 0.242 | 0.239 | 0.236 | 0.23
| 14 | 0.254 | 0.247 | 0.24 | 0.233 | 0.227 | 0.221 | 0.215 | 0.213 | 0.21 | 0.205
| 14.5 | 0.227 | 0.221 | 0.214 | 0.209 | 0.203 | 0.198 | 0.193 | 0.19 | 0.188 | 0.184
| 15 | 0.204 | 0.198 | 0.193 | 0.188 | 0.183 | 0.178 | 0.174 | 0.171 | 0.169 | 0.165
| 15.5 | 0.184 | 0.179 | 0.174 | 0.17 | 0.165 | 0.161 | 0.157 | 0.155 | 0.153 | 0.15
| 16 | 0.167 | 0.163 | 0.158 | 0.154 | 0.15 | 0.146 | 0.143 | 0.141 | 0.139 | 0.136
| 16.5 | 0.153 | 0.148 | 0.144 | 0.141 | 0.137 | 0.134 | 0.13 | 0.129 | 0.127 | 0.125
| 17 | 0.14 | 0.136 | 0.132 | 0.129 | 0.126 | 0.123 | 0.12 | 0.118 | 0.117 | 0.114
| 17.5 | 0.129 | 0.126 | 0.122 | 0.119 | 0.116 | 0.113 | 0.111 | 0.109 | 0.108 | 0.106
| 18 | 0.12 | 0.116 | 0.113 | 0.11 | 0.108 | 0.105 | 0.103 | 0.101 | 0.1 | 0.098
| 18.5 | 0.111 | 0.108 | 0.106 | 0.103 | 0.1 | 0.098 | 0.096 | 0.095 | 0.094 | 0.091
| 19 | 0.104 | 0.101 | 0.099 | 0.096 | 0.094 | 0.092 | 0.09 | 0.089 | 0.088 | 0.086
| 19.5 | 0.098 | 0.095 | 0.093 | 0.091 | 0.088 | 0.086 | 0.084 | 0.083 | 0.082 | 0.081
| 20 | 0.092 | 0.09 | 0.087 | 0.085 | 0.083 | 0.081 | 0.079 | 0.078 | 0.078 | 0.076
| 20.5 | 0.078 | 0.076 | 0.074 | 0.072 | 0.07 | 0.069 | 0.067 | 0.067 | 0.066 | 0.065
| 21 | 0.071 | 0.069 | 0.068 | 0.066 | 0.065 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059
| 21.5 | 0.065 | 0.064 | 0.062 | 0.061 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054
| 22 | 0.06 | 0.058 | 0.057 | 0.056 | 0.054 | 0.053 | 0.052 | 0.052 | 0.051 | 0.05
| 22.5 | 0.055 | 0.054 | 0.053 | 0.051 | 0.05 | 0.049 | 0.048 | 0.048 | 0.047 | 0.046
| 23 | 0.051 | 0.05 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.044 | 0.043 | 0.043
| 23.5 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.041 | 0.04 | 0.039
| 24 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037 | 0.036
| 24.5 | 0.04 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.034
| 25 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.032 | 0.031