## Sheet1
PROPERTIES
General
Name | Gamesa SG 6.6-170 -MOD 6,4 MW_v2
Manufacturer | Gamesa
Hub Height | 100 | 115 | 135 | 145 | 155 | 165
Power
Rated Power | 6400
Peak Power | 6400
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 170
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 25
Restart Wind Speed | 22
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -30
Low Temperature Restart | -20
High Temperature Shutdown | 50
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 7.38
Vref | 42.5
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.03 | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.24 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 72 | 75 | 77 | 80 | 82 | 85 | 88 | 89 | 90 | 93
| 3.5 | 139 | 145 | 151 | 157 | 163 | 169 | 175 | 178 | 181 | 187
| 4 | 261 | 272 | 282 | 292 | 302 | 312 | 323 | 328 | 333 | 343
| 4.5 | 424 | 439 | 454 | 470 | 485 | 500 | 515 | 522 | 530 | 545
| 5 | 624 | 645 | 665 | 686 | 707 | 728 | 749 | 759 | 769 | 790
| 5.5 | 866 | 894 | 921 | 949 | 977 | 1005 | 1033 | 1046 | 1060 | 1088
| 6 | 1157 | 1194 | 1230 | 1266 | 1303 | 1339 | 1375 | 1393 | 1411 | 1448
| 6.5 | 1500 | 1547 | 1593 | 1639 | 1685 | 1732 | 1778 | 1801 | 1824 | 1870
| 7 | 1897 | 1955 | 2012 | 2070 | 2128 | 2186 | 2243 | 2272 | 2301 | 2358
| 7.5 | 2350 | 2421 | 2491 | 2562 | 2633 | 2703 | 2774 | 2809 | 2844 | 2914
| 8 | 2855 | 2940 | 3025 | 3110 | 3195 | 3280 | 3364 | 3407 | 3449 | 3533
| 8.5 | 3397 | 3498 | 3598 | 3698 | 3797 | 3896 | 3994 | 4043 | 4091 | 4186
| 9 | 3950 | 4066 | 4181 | 4294 | 4406 | 4515 | 4621 | 4673 | 4723 | 4822
| 9.5 | 4483 | 4612 | 4738 | 4859 | 4975 | 5085 | 5187 | 5236 | 5284 | 5372
| 10 | 4968 | 5104 | 5232 | 5350 | 5458 | 5555 | 5642 | 5682 | 5720 | 5789
| 10.5 | 5384 | 5515 | 5633 | 5736 | 5824 | 5899 | 5963 | 5992 | 6019 | 6066
| 11 | 5717 | 5832 | 5929 | 6008 | 6072 | 6124 | 6166 | 6184 | 6201 | 6230
| 11.5 | 5966 | 6057 | 6129 | 6183 | 6225 | 6257 | 6282 | 6293 | 6302 | 6318
| 12 | 6139 | 6204 | 6252 | 6286 | 6311 | 6329 | 6343 | 6349 | 6354 | 6362
| 12.5 | 6251 | 6293 | 6323 | 6343 | 6357 | 6366 | 6373 | 6376 | 6379 | 6383
| 13 | 6318 | 6344 | 6361 | 6372 | 6379 | 6384 | 6388 | 6389 | 6391 | 6392
| 13.5 | 6357 | 6372 | 6381 | 6387 | 6390 | 6393 | 6395 | 6395 | 6396 | 6397
| 14 | 6378 | 6386 | 6391 | 6394 | 6396 | 6397 | 6398 | 6398 | 6398 | 6399
| 14.5 | 6389 | 6393 | 6396 | 6397 | 6398 | 6399 | 6399 | 6399 | 6399 | 6399
| 15 | 6394 | 6397 | 6398 | 6399 | 6399 | 6399 | 6400 | 6400 | 6400 | 6400
| 15.5 | 6397 | 6398 | 6399 | 6399 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400
| 16 | 6399 | 6399 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400
| 16.5 | 6399 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400
| 17 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400
| 17.5 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400
| 18 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400
| 18.5 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400
| 19 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400
| 19.5 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400
| 20 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400 | 6400
| 20.5 | 6272 | 6272 | 6272 | 6272 | 6272 | 6272 | 6272 | 6272 | 6272 | 6272
| 21 | 6144 | 6144 | 6144 | 6144 | 6144 | 6144 | 6144 | 6144 | 6144 | 6144
| 21.5 | 6016 | 6016 | 6016 | 6016 | 6016 | 6016 | 6016 | 6016 | 6016 | 6016
| 22 | 5888 | 5888 | 5888 | 5888 | 5888 | 5888 | 5888 | 5888 | 5888 | 5888
| 22.5 | 5760 | 5760 | 5760 | 5760 | 5760 | 5760 | 5760 | 5760 | 5760 | 5760
| 23 | 5632 | 5632 | 5632 | 5632 | 5632 | 5632 | 5632 | 5632 | 5632 | 5632
| 23.5 | 5504 | 5504 | 5504 | 5504 | 5504 | 5504 | 5504 | 5504 | 5504 | 5504
| 24 | 5376 | 5376 | 5376 | 5376 | 5376 | 5376 | 5376 | 5376 | 5376 | 5376
| 24.5 | 5248 | 5248 | 5248 | 5248 | 5248 | 5248 | 5248 | 5248 | 5248 | 5248
| 25 | 5120 | 5120 | 5120 | 5120 | 5120 | 5120 | 5120 | 5120 | 5120 | 5120

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.03 | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.24 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953
| 3.5 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
| 4 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847
| 4.5 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828
| 5 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824
| 5.5 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828
| 6 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833
| 6.5 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836
| 7 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837
| 7.5 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835
| 8 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825
| 8.5 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.803 | 0.803 | 0.803 | 0.802 | 0.801
| 9 | 0.767 | 0.767 | 0.767 | 0.767 | 0.766 | 0.765 | 0.764 | 0.763 | 0.761 | 0.758
| 9.5 | 0.717 | 0.717 | 0.716 | 0.715 | 0.713 | 0.71 | 0.706 | 0.704 | 0.701 | 0.695
| 10 | 0.658 | 0.657 | 0.655 | 0.652 | 0.648 | 0.642 | 0.635 | 0.631 | 0.627 | 0.619
| 10.5 | 0.595 | 0.592 | 0.588 | 0.583 | 0.576 | 0.568 | 0.559 | 0.554 | 0.549 | 0.539
| 11 | 0.532 | 0.528 | 0.522 | 0.514 | 0.506 | 0.496 | 0.486 | 0.48 | 0.475 | 0.464
| 11.5 | 0.473 | 0.467 | 0.459 | 0.45 | 0.44 | 0.43 | 0.42 | 0.415 | 0.41 | 0.4
| 12 | 0.419 | 0.411 | 0.402 | 0.393 | 0.383 | 0.374 | 0.364 | 0.359 | 0.355 | 0.346
| 12.5 | 0.37 | 0.362 | 0.353 | 0.344 | 0.335 | 0.326 | 0.317 | 0.313 | 0.309 | 0.301
| 13 | 0.327 | 0.319 | 0.31 | 0.302 | 0.294 | 0.286 | 0.278 | 0.275 | 0.271 | 0.264
| 13.5 | 0.29 | 0.282 | 0.274 | 0.267 | 0.26 | 0.253 | 0.246 | 0.243 | 0.24 | 0.234
| 14 | 0.258 | 0.251 | 0.244 | 0.237 | 0.231 | 0.225 | 0.219 | 0.216 | 0.213 | 0.208
| 14.5 | 0.231 | 0.224 | 0.218 | 0.212 | 0.206 | 0.201 | 0.196 | 0.194 | 0.191 | 0.187
| 15 | 0.207 | 0.202 | 0.196 | 0.191 | 0.186 | 0.181 | 0.176 | 0.174 | 0.172 | 0.168
| 15.5 | 0.187 | 0.182 | 0.177 | 0.172 | 0.168 | 0.164 | 0.16 | 0.158 | 0.156 | 0.152
| 16 | 0.17 | 0.165 | 0.161 | 0.156 | 0.152 | 0.149 | 0.145 | 0.143 | 0.142 | 0.138
| 16.5 | 0.155 | 0.151 | 0.147 | 0.143 | 0.139 | 0.136 | 0.132 | 0.131 | 0.129 | 0.126
| 17 | 0.142 | 0.138 | 0.135 | 0.131 | 0.128 | 0.125 | 0.122 | 0.12 | 0.119 | 0.116
| 17.5 | 0.131 | 0.127 | 0.124 | 0.121 | 0.118 | 0.115 | 0.112 | 0.111 | 0.11 | 0.107
| 18 | 0.121 | 0.118 | 0.115 | 0.112 | 0.109 | 0.107 | 0.104 | 0.103 | 0.102 | 0.1
| 18.5 | 0.113 | 0.11 | 0.107 | 0.104 | 0.102 | 0.099 | 0.097 | 0.096 | 0.095 | 0.093
| 19 | 0.106 | 0.103 | 0.1 | 0.098 | 0.095 | 0.093 | 0.091 | 0.09 | 0.089 | 0.087
| 19.5 | 0.099 | 0.097 | 0.094 | 0.092 | 0.09 | 0.087 | 0.085 | 0.084 | 0.084 | 0.082
| 20 | 0.094 | 0.091 | 0.089 | 0.087 | 0.084 | 0.082 | 0.081 | 0.08 | 0.079 | 0.077
| 20.5 | 0.079 | 0.077 | 0.075 | 0.073 | 0.071 | 0.07 | 0.068 | 0.068 | 0.067 | 0.065
| 21 | 0.072 | 0.07 | 0.069 | 0.067 | 0.065 | 0.064 | 0.063 | 0.062 | 0.061 | 0.06
| 21.5 | 0.066 | 0.065 | 0.063 | 0.061 | 0.06 | 0.059 | 0.057 | 0.057 | 0.056 | 0.055
| 22 | 0.061 | 0.059 | 0.058 | 0.057 | 0.055 | 0.054 | 0.053 | 0.052 | 0.052 | 0.051
| 22.5 | 0.056 | 0.055 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.048 | 0.047
| 23 | 0.052 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.044 | 0.043
| 23.5 | 0.048 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.042 | 0.041 | 0.041 | 0.04
| 24 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.038 | 0.038 | 0.038 | 0.037
| 24.5 | 0.041 | 0.04 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.035 | 0.034
| 25 | 0.038 | 0.037 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.033 | 0.032 | 0.032