## Sheet1
PROPERTIES
General
Name | Gamesa SG 6.6-170 -MOD 6,5 MW_v2
Manufacturer | Gamesa
Hub Height | 100 | 115 | 135 | 145 | 155 | 165
Power
Rated Power | 6500
Peak Power | 6500
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 170
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 25
Restart Wind Speed | 22
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -30
Low Temperature Restart | -20
High Temperature Shutdown | 50
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 7.38
Vref | 42.5
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.03 | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.24 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 72 | 75 | 77 | 80 | 82 | 85 | 88 | 89 | 90 | 93
| 3.5 | 139 | 145 | 151 | 157 | 163 | 169 | 175 | 178 | 181 | 187
| 4 | 261 | 272 | 282 | 292 | 302 | 312 | 323 | 328 | 333 | 343
| 4.5 | 424 | 439 | 454 | 470 | 485 | 500 | 515 | 522 | 530 | 545
| 5 | 624 | 645 | 665 | 686 | 707 | 728 | 749 | 759 | 769 | 790
| 5.5 | 866 | 894 | 921 | 949 | 977 | 1005 | 1033 | 1046 | 1060 | 1088
| 6 | 1157 | 1194 | 1230 | 1266 | 1303 | 1339 | 1375 | 1393 | 1411 | 1448
| 6.5 | 1500 | 1547 | 1593 | 1639 | 1685 | 1732 | 1778 | 1801 | 1824 | 1870
| 7 | 1897 | 1955 | 2012 | 2070 | 2128 | 2186 | 2243 | 2272 | 2301 | 2358
| 7.5 | 2350 | 2421 | 2491 | 2562 | 2633 | 2703 | 2774 | 2809 | 2844 | 2914
| 8 | 2855 | 2940 | 3025 | 3110 | 3195 | 3280 | 3365 | 3407 | 3449 | 3533
| 8.5 | 3397 | 3498 | 3598 | 3698 | 3798 | 3897 | 3995 | 4044 | 4093 | 4189
| 9 | 3950 | 4066 | 4181 | 4296 | 4408 | 4519 | 4627 | 4680 | 4732 | 4833
| 9.5 | 4484 | 4613 | 4741 | 4865 | 4984 | 5098 | 5204 | 5255 | 5305 | 5398
| 10 | 4971 | 5109 | 5242 | 5366 | 5480 | 5583 | 5676 | 5719 | 5760 | 5834
| 10.5 | 5392 | 5530 | 5655 | 5767 | 5863 | 5946 | 6017 | 6049 | 6078 | 6130
| 11 | 5737 | 5862 | 5969 | 6058 | 6130 | 6189 | 6237 | 6257 | 6276 | 6308
| 11.5 | 6002 | 6104 | 6186 | 6250 | 6298 | 6336 | 6365 | 6377 | 6388 | 6406
| 12 | 6191 | 6267 | 6324 | 6366 | 6396 | 6418 | 6434 | 6441 | 6447 | 6456
| 12.5 | 6318 | 6370 | 6406 | 6431 | 6448 | 6460 | 6469 | 6472 | 6475 | 6480
| 13 | 6397 | 6430 | 6452 | 6466 | 6475 | 6481 | 6486 | 6487 | 6489 | 6491
| 13.5 | 6444 | 6464 | 6476 | 6483 | 6488 | 6491 | 6493 | 6494 | 6495 | 6496
| 14 | 6471 | 6482 | 6488 | 6492 | 6495 | 6496 | 6497 | 6497 | 6498 | 6498
| 14.5 | 6485 | 6491 | 6494 | 6496 | 6497 | 6498 | 6499 | 6499 | 6499 | 6499
| 15 | 6492 | 6495 | 6497 | 6498 | 6499 | 6499 | 6499 | 6499 | 6500 | 6500
| 15.5 | 6496 | 6498 | 6499 | 6499 | 6499 | 6500 | 6500 | 6500 | 6500 | 6500
| 16 | 6498 | 6499 | 6499 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500
| 16.5 | 6499 | 6499 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500
| 17 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500
| 17.5 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500
| 18 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500
| 18.5 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500
| 19 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500
| 19.5 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500
| 20 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500 | 6500
| 20.5 | 6370 | 6370 | 6370 | 6370 | 6370 | 6370 | 6370 | 6370 | 6370 | 6370
| 21 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240
| 21.5 | 6110 | 6110 | 6110 | 6110 | 6110 | 6110 | 6110 | 6110 | 6110 | 6110
| 22 | 5980 | 5980 | 5980 | 5980 | 5980 | 5980 | 5980 | 5980 | 5980 | 5980
| 22.5 | 5850 | 5850 | 5850 | 5850 | 5850 | 5850 | 5850 | 5850 | 5850 | 5850
| 23 | 5720 | 5720 | 5720 | 5720 | 5720 | 5720 | 5720 | 5720 | 5720 | 5720
| 23.5 | 5590 | 5590 | 5590 | 5590 | 5590 | 5590 | 5590 | 5590 | 5590 | 5590
| 24 | 5460 | 5460 | 5460 | 5460 | 5460 | 5460 | 5460 | 5460 | 5460 | 5460
| 24.5 | 5330 | 5330 | 5330 | 5330 | 5330 | 5330 | 5330 | 5330 | 5330 | 5330
| 25 | 5200 | 5200 | 5200 | 5200 | 5200 | 5200 | 5200 | 5200 | 5200 | 5200

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.03 | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.24 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953
| 3.5 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
| 4 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847
| 4.5 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828
| 5 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824
| 5.5 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828
| 6 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833
| 6.5 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836
| 7 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837
| 7.5 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835
| 8 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825
| 8.5 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.803 | 0.803 | 0.803 | 0.803 | 0.802
| 9 | 0.767 | 0.767 | 0.767 | 0.767 | 0.767 | 0.766 | 0.765 | 0.764 | 0.763 | 0.76
| 9.5 | 0.717 | 0.717 | 0.717 | 0.716 | 0.714 | 0.712 | 0.709 | 0.707 | 0.705 | 0.699
| 10 | 0.658 | 0.657 | 0.656 | 0.654 | 0.65 | 0.645 | 0.639 | 0.636 | 0.632 | 0.624
| 10.5 | 0.596 | 0.594 | 0.591 | 0.586 | 0.58 | 0.573 | 0.565 | 0.56 | 0.556 | 0.546
| 11 | 0.534 | 0.531 | 0.525 | 0.519 | 0.511 | 0.502 | 0.492 | 0.487 | 0.482 | 0.471
| 11.5 | 0.476 | 0.47 | 0.463 | 0.455 | 0.446 | 0.436 | 0.426 | 0.421 | 0.416 | 0.406
| 12 | 0.422 | 0.415 | 0.407 | 0.398 | 0.389 | 0.379 | 0.37 | 0.365 | 0.361 | 0.352
| 12.5 | 0.374 | 0.366 | 0.358 | 0.349 | 0.34 | 0.331 | 0.322 | 0.318 | 0.314 | 0.306
| 13 | 0.331 | 0.323 | 0.315 | 0.307 | 0.298 | 0.291 | 0.283 | 0.279 | 0.276 | 0.269
| 13.5 | 0.294 | 0.286 | 0.279 | 0.271 | 0.264 | 0.257 | 0.25 | 0.247 | 0.244 | 0.238
| 14 | 0.262 | 0.255 | 0.248 | 0.241 | 0.234 | 0.228 | 0.222 | 0.22 | 0.217 | 0.212
| 14.5 | 0.235 | 0.228 | 0.221 | 0.215 | 0.21 | 0.204 | 0.199 | 0.197 | 0.194 | 0.19
| 15 | 0.211 | 0.205 | 0.199 | 0.194 | 0.189 | 0.184 | 0.179 | 0.177 | 0.175 | 0.171
| 15.5 | 0.19 | 0.185 | 0.18 | 0.175 | 0.17 | 0.166 | 0.162 | 0.16 | 0.158 | 0.154
| 16 | 0.173 | 0.168 | 0.163 | 0.159 | 0.155 | 0.151 | 0.147 | 0.145 | 0.144 | 0.14
| 16.5 | 0.157 | 0.153 | 0.149 | 0.145 | 0.141 | 0.138 | 0.134 | 0.133 | 0.131 | 0.128
| 17 | 0.144 | 0.14 | 0.137 | 0.133 | 0.13 | 0.126 | 0.123 | 0.122 | 0.121 | 0.118
| 17.5 | 0.133 | 0.129 | 0.126 | 0.123 | 0.12 | 0.117 | 0.114 | 0.113 | 0.111 | 0.109
| 18 | 0.123 | 0.12 | 0.117 | 0.114 | 0.111 | 0.108 | 0.106 | 0.104 | 0.103 | 0.101
| 18.5 | 0.115 | 0.112 | 0.109 | 0.106 | 0.103 | 0.101 | 0.099 | 0.097 | 0.096 | 0.094
| 19 | 0.107 | 0.105 | 0.102 | 0.099 | 0.097 | 0.094 | 0.092 | 0.091 | 0.09 | 0.088
| 19.5 | 0.101 | 0.098 | 0.096 | 0.093 | 0.091 | 0.089 | 0.087 | 0.086 | 0.085 | 0.083
| 20 | 0.095 | 0.092 | 0.09 | 0.088 | 0.086 | 0.084 | 0.082 | 0.081 | 0.08 | 0.078
| 20.5 | 0.08 | 0.078 | 0.076 | 0.074 | 0.072 | 0.071 | 0.069 | 0.069 | 0.068 | 0.066
| 21 | 0.073 | 0.071 | 0.07 | 0.068 | 0.066 | 0.065 | 0.063 | 0.063 | 0.062 | 0.061
| 21.5 | 0.067 | 0.065 | 0.064 | 0.062 | 0.061 | 0.059 | 0.058 | 0.058 | 0.057 | 0.056
| 22 | 0.062 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051
| 22.5 | 0.057 | 0.055 | 0.054 | 0.053 | 0.052 | 0.05 | 0.049 | 0.049 | 0.048 | 0.047
| 23 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.046 | 0.046 | 0.045 | 0.045 | 0.044
| 23.5 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.042 | 0.041 | 0.04
| 24 | 0.045 | 0.043 | 0.042 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.038 | 0.037
| 24.5 | 0.041 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.035
| 25 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.033 | 0.033 | 0.033 | 0.032