## Sheet1
PROPERTIES
General
Name | Gamesa SG 6.6-170 -MOD 6,6 MW_v2
Manufacturer | Gamesa
Hub Height | 100 | 115 | 135 | 145 | 155 | 165
Power
Rated Power | 6600
Peak Power | 6600
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 170
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 25
Restart Wind Speed | 22
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -30
Low Temperature Restart | -20
High Temperature Shutdown | 50
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 7.38
Vref | 42.5
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.03 | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 72 | 75 | 77 | 80 | 82 | 85 | 88 | 89 | 93
| 3.5 | 139 | 145 | 151 | 157 | 163 | 169 | 175 | 178 | 187
| 4 | 261 | 272 | 282 | 292 | 302 | 312 | 323 | 328 | 343
| 4.5 | 424 | 439 | 454 | 470 | 485 | 500 | 515 | 522 | 545
| 5 | 624 | 645 | 665 | 686 | 707 | 728 | 749 | 759 | 790
| 5.5 | 866 | 894 | 921 | 949 | 977 | 1005 | 1033 | 1046 | 1088
| 6 | 1157 | 1194 | 1230 | 1266 | 1303 | 1339 | 1375 | 1393 | 1448
| 6.5 | 1500 | 1547 | 1593 | 1639 | 1685 | 1732 | 1778 | 1801 | 1870
| 7 | 1897 | 1955 | 2012 | 2070 | 2128 | 2186 | 2243 | 2272 | 2358
| 7.5 | 2350 | 2421 | 2491 | 2562 | 2633 | 2703 | 2774 | 2809 | 2915
| 8 | 2855 | 2940 | 3025 | 3110 | 3195 | 3280 | 3365 | 3407 | 3533
| 8.5 | 3397 | 3498 | 3598 | 3698 | 3798 | 3897 | 3996 | 4045 | 4191
| 9 | 3950 | 4066 | 4181 | 4296 | 4410 | 4522 | 4632 | 4685 | 4842
| 9.5 | 4484 | 4614 | 4743 | 4869 | 4991 | 5108 | 5219 | 5272 | 5421
| 10 | 4973 | 5113 | 5249 | 5378 | 5498 | 5608 | 5707 | 5753 | 5876
| 10.5 | 5399 | 5541 | 5674 | 5793 | 5898 | 5989 | 6067 | 6101 | 6191
| 11 | 5753 | 5886 | 6003 | 6102 | 6184 | 6250 | 6304 | 6327 | 6385
| 11.5 | 6031 | 6145 | 6237 | 6311 | 6368 | 6412 | 6445 | 6460 | 6493
| 12 | 6238 | 6325 | 6391 | 6441 | 6478 | 6504 | 6523 | 6531 | 6549
| 12.5 | 6380 | 6442 | 6486 | 6517 | 6538 | 6553 | 6563 | 6567 | 6577
| 13 | 6473 | 6513 | 6540 | 6558 | 6570 | 6577 | 6583 | 6585 | 6590
| 13.5 | 6529 | 6554 | 6569 | 6579 | 6586 | 6589 | 6592 | 6593 | 6595
| 14 | 6562 | 6576 | 6585 | 6590 | 6593 | 6595 | 6596 | 6597 | 6598
| 14.5 | 6580 | 6588 | 6592 | 6595 | 6597 | 6598 | 6598 | 6599 | 6599
| 15 | 6590 | 6594 | 6596 | 6598 | 6599 | 6599 | 6599 | 6599 | 6600
| 15.5 | 6595 | 6597 | 6598 | 6599 | 6599 | 6600 | 6600 | 6600 | 6600
| 16 | 6597 | 6599 | 6599 | 6599 | 6600 | 6600 | 6600 | 6600 | 6600
| 16.5 | 6599 | 6599 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600
| 17 | 6599 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600
| 17.5 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600
| 18 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600
| 18.5 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600
| 19 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600
| 19.5 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600
| 20 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600 | 6600
| 20.5 | 6468 | 6468 | 6468 | 6468 | 6468 | 6468 | 6468 | 6468 | 6468
| 21 | 6336 | 6336 | 6336 | 6336 | 6336 | 6336 | 6336 | 6336 | 6336
| 21.5 | 6204 | 6204 | 6204 | 6204 | 6204 | 6204 | 6204 | 6204 | 6204
| 22 | 6072 | 6072 | 6072 | 6072 | 6072 | 6072 | 6072 | 6072 | 6072
| 22.5 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 23 | 5808 | 5808 | 5808 | 5808 | 5808 | 5808 | 5808 | 5808 | 5808
| 23.5 | 5676 | 5676 | 5676 | 5676 | 5676 | 5676 | 5676 | 5676 | 5676
| 24 | 5544 | 5544 | 5544 | 5544 | 5544 | 5544 | 5544 | 5544 | 5544
| 24.5 | 5412 | 5412 | 5412 | 5412 | 5412 | 5412 | 5412 | 5412 | 5412
| 25 | 5280 | 5280 | 5280 | 5280 | 5280 | 5280 | 5280 | 5280 | 5280

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.03 | 1.06 | 1.09 | 1.12 | 1.15 | 1.18 | 1.21 | 1.225 | 1.27
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953
| 3.5 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
| 4 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847 | 0.847
| 4.5 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828
| 5 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824
| 5.5 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828 | 0.828
| 6 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833 | 0.833
| 6.5 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836 | 0.836
| 7 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837 | 0.837
| 7.5 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835 | 0.835
| 8 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825
| 8.5 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.803 | 0.803 | 0.803
| 9 | 0.767 | 0.767 | 0.767 | 0.767 | 0.767 | 0.766 | 0.765 | 0.765 | 0.762
| 9.5 | 0.717 | 0.717 | 0.717 | 0.716 | 0.715 | 0.713 | 0.711 | 0.709 | 0.703
| 10 | 0.658 | 0.658 | 0.657 | 0.655 | 0.652 | 0.648 | 0.643 | 0.64 | 0.63
| 10.5 | 0.596 | 0.595 | 0.593 | 0.589 | 0.584 | 0.578 | 0.57 | 0.566 | 0.552
| 11 | 0.535 | 0.533 | 0.528 | 0.523 | 0.516 | 0.507 | 0.498 | 0.493 | 0.478
| 11.5 | 0.478 | 0.474 | 0.467 | 0.46 | 0.451 | 0.442 | 0.433 | 0.428 | 0.413
| 12 | 0.425 | 0.419 | 0.412 | 0.403 | 0.394 | 0.385 | 0.376 | 0.371 | 0.357
| 12.5 | 0.378 | 0.371 | 0.362 | 0.354 | 0.345 | 0.336 | 0.328 | 0.323 | 0.311
| 13 | 0.335 | 0.328 | 0.32 | 0.311 | 0.303 | 0.295 | 0.288 | 0.284 | 0.273
| 13.5 | 0.298 | 0.291 | 0.283 | 0.275 | 0.268 | 0.261 | 0.254 | 0.251 | 0.242
| 14 | 0.266 | 0.259 | 0.252 | 0.245 | 0.238 | 0.232 | 0.226 | 0.223 | 0.215
| 14.5 | 0.238 | 0.231 | 0.225 | 0.219 | 0.213 | 0.207 | 0.202 | 0.2 | 0.192
| 15 | 0.214 | 0.208 | 0.202 | 0.197 | 0.191 | 0.187 | 0.182 | 0.18 | 0.173
| 15.5 | 0.193 | 0.188 | 0.183 | 0.178 | 0.173 | 0.169 | 0.164 | 0.162 | 0.157
| 16 | 0.175 | 0.17 | 0.166 | 0.161 | 0.157 | 0.153 | 0.149 | 0.148 | 0.143
| 16.5 | 0.16 | 0.155 | 0.151 | 0.147 | 0.143 | 0.14 | 0.136 | 0.135 | 0.13
| 17 | 0.147 | 0.142 | 0.139 | 0.135 | 0.132 | 0.128 | 0.125 | 0.124 | 0.12
| 17.5 | 0.135 | 0.131 | 0.128 | 0.125 | 0.121 | 0.118 | 0.116 | 0.114 | 0.11
| 18 | 0.125 | 0.122 | 0.118 | 0.115 | 0.113 | 0.11 | 0.107 | 0.106 | 0.102
| 18.5 | 0.117 | 0.113 | 0.11 | 0.108 | 0.105 | 0.102 | 0.1 | 0.099 | 0.096
| 19 | 0.109 | 0.106 | 0.103 | 0.101 | 0.098 | 0.096 | 0.094 | 0.093 | 0.089
| 19.5 | 0.102 | 0.1 | 0.097 | 0.095 | 0.092 | 0.09 | 0.088 | 0.087 | 0.084
| 20 | 0.096 | 0.094 | 0.091 | 0.089 | 0.087 | 0.085 | 0.083 | 0.082 | 0.079
| 20.5 | 0.081 | 0.079 | 0.077 | 0.075 | 0.073 | 0.072 | 0.07 | 0.069 | 0.067
| 21 | 0.074 | 0.072 | 0.071 | 0.069 | 0.067 | 0.066 | 0.064 | 0.064 | 0.062
| 21.5 | 0.068 | 0.066 | 0.065 | 0.063 | 0.062 | 0.06 | 0.059 | 0.058 | 0.057
| 22 | 0.063 | 0.061 | 0.059 | 0.058 | 0.057 | 0.055 | 0.054 | 0.054 | 0.052
| 22.5 | 0.057 | 0.056 | 0.055 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048
| 23 | 0.053 | 0.052 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.046 | 0.044
| 23.5 | 0.049 | 0.048 | 0.047 | 0.045 | 0.044 | 0.044 | 0.043 | 0.042 | 0.041
| 24 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.038
| 24.5 | 0.042 | 0.041 | 0.04 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036 | 0.035
| 25 | 0.039 | 0.038 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.034 | 0.033