## Sheet1
PROPERTIES
General
Name | Gamesa SG 7,0-170 -MOD 7,0 MW_v2
Manufacturer | Gamesa
Hub Height | 112.5 | 115 | 135 | 155 | 165 | 185
Power
Rated Power | 7000
Peak Power | 7000
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 170
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 25
Restart Wind Speed | 22
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -30
Low Temperature Restart | -20
High Temperature Shutdown | 50
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | 2A
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 8.5
Vref | 42.5
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.225
Wind Speed (m/s) | 0 | 0
| 0.5 | 0
| 1 | 0
| 1.5 | 0
| 2 | 0
| 2.5 | 0
| 3 | 0
| 3.5 | 148
| 4 | 310
| 4.5 | 510
| 5 | 751
| 5.5 | 1037
| 6 | 1374
| 6.5 | 1768
| 7 | 2221
| 7.5 | 2736
| 8 | 3318
| 8.5 | 3967
| 9 | 4659
| 9.5 | 5342
| 10 | 5950
| 10.5 | 6422
| 11 | 6728
| 11.5 | 6891
| 12 | 6962
| 12.5 | 6988
| 13 | 6997
| 13.5 | 6999
| 14 | 7000
| 14.5 | 7000
| 15 | 7000
| 15.5 | 7000
| 16 | 7000
| 16.5 | 7000
| 17 | 7000
| 17.5 | 7000
| 18 | 7000
| 18.5 | 7000
| 19 | 7000
| 19.5 | 7000
| 20 | 6737
| 20.5 | 6475
| 21 | 6212
| 21.5 | 5950
| 22 | 5687
| 22.5 | 5425
| 23 | 5162
| 23.5 | 4900
| 24 | 4900
| 24.5 | 4900
| 25 | 4900

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
1.225
Wind Speed (m/s) | 0 | 0
| 0.5 | 0
| 1 | 0
| 1.5 | 0
| 2 | 0
| 2.5 | 0
| 3 | 0
| 3.5 | 0.9291
| 4 | 0.8698
| 4.5 | 0.8407
| 5 | 0.826
| 5.5 | 0.8199
| 6 | 0.8213
| 6.5 | 0.8191
| 7 | 0.8143
| 7.5 | 0.8079
| 8 | 0.7979
| 8.5 | 0.784
| 9 | 0.7624
| 9.5 | 0.7256
| 10 | 0.6724
| 10.5 | 0.6085
| 11 | 0.5403
| 11.5 | 0.4732
| 12 | 0.4117
| 12.5 | 0.3585
| 13 | 0.3139
| 13.5 | 0.2768
| 14 | 0.2459
| 14.5 | 0.2198
| 15 | 0.1976
| 15.5 | 0.1786
| 16 | 0.1621
| 16.5 | 0.1477
| 17 | 0.1351
| 17.5 | 0.124
| 18 | 0.1142
| 18.5 | 0.1055
| 19 | 0.0977
| 19.5 | 0.0907
| 20 | 0.0812
| 20.5 | 0.0728
| 21 | 0.0653
| 21.5 | 0.0586
| 22 | 0.0526
| 22.5 | 0.0473
| 23 | 0.0425
| 23.5 | 0.0383
| 24 | 0.0366
| 24.5 | 0.0351
| 25 | 0.034