## Sheet1
PROPERTIES
General
Name | N163-6.X MW 50-60 Hz vM0_7000
Manufacturer | Nordex
Hub Height | 118 | 138 | 148 | 158.5 | 164
Power
Rated Power | 7000
Peak Power | 7000
Power Regulation Type | Pitch
Voltage | 920
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | -
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -40
Low Temperature Restart | -20
High Temperature Shutdown | 40
High Temperature Restart | 50
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 39.5
Design TI | 0.35

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 5 | 7 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 28 | 30 | 32 | 34 | 37 | 39
| 3.5 | 81 | 85 | 89 | 93 | 97 | 102 | 106 | 110 | 114 | 118 | 122 | 127 | 131 | 135 | 139 | 143 | 147
| 4 | 183 | 190 | 197 | 204 | 211 | 218 | 225 | 232 | 239 | 246 | 253 | 260 | 267 | 274 | 281 | 288 | 295
| 4.5 | 311 | 322 | 332 | 343 | 353 | 364 | 374 | 385 | 396 | 406 | 417 | 427 | 438 | 448 | 459 | 469 | 480
| 5 | 465 | 480 | 495 | 509 | 524 | 539 | 554 | 569 | 583 | 598 | 613 | 628 | 643 | 657 | 672 | 687 | 702
| 5.5 | 647 | 667 | 687 | 706 | 726 | 746 | 766 | 786 | 806 | 826 | 845 | 865 | 885 | 905 | 925 | 944 | 964
| 6 | 862 | 887 | 913 | 939 | 965 | 991 | 1016 | 1042 | 1068 | 1094 | 1119 | 1145 | 1171 | 1197 | 1222 | 1248 | 1274
| 6.5 | 1114 | 1146 | 1179 | 1212 | 1245 | 1277 | 1310 | 1343 | 1375 | 1408 | 1441 | 1473 | 1506 | 1539 | 1571 | 1604 | 1637
| 7 | 1407 | 1448 | 1488 | 1529 | 1570 | 1611 | 1652 | 1692 | 1733 | 1774 | 1814 | 1855 | 1896 | 1937 | 1977 | 2018 | 2059
| 7.5 | 1744 | 1795 | 1845 | 1895 | 1945 | 1995 | 2045 | 2095 | 2145 | 2195 | 2245 | 2294 | 2344 | 2394 | 2444 | 2494 | 2544
| 8 | 2129 | 2190 | 2250 | 2311 | 2372 | 2432 | 2493 | 2553 | 2614 | 2674 | 2734 | 2795 | 2855 | 2916 | 2976 | 3036 | 3096
| 8.5 | 2562 | 2635 | 2707 | 2779 | 2852 | 2924 | 2996 | 3069 | 3141 | 3213 | 3285 | 3357 | 3427 | 3495 | 3562 | 3627 | 3690
| 9 | 3026 | 3111 | 3196 | 3281 | 3366 | 3451 | 3536 | 3620 | 3705 | 3790 | 3875 | 3954 | 4027 | 4097 | 4164 | 4229 | 4291
| 9.5 | 3494 | 3592 | 3689 | 3787 | 3885 | 3982 | 4080 | 4177 | 4275 | 4372 | 4469 | 4554 | 4625 | 4693 | 4757 | 4819 | 4876
| 10 | 3951 | 4061 | 4171 | 4281 | 4391 | 4501 | 4611 | 4721 | 4830 | 4939 | 5049 | 5140 | 5207 | 5270 | 5329 | 5385 | 5436
| 10.5 | 4388 | 4510 | 4631 | 4753 | 4875 | 4997 | 5118 | 5239 | 5362 | 5484 | 5601 | 5688 | 5745 | 5798 | 5848 | 5893 | 5935
| 11 | 4794 | 4927 | 5060 | 5192 | 5325 | 5457 | 5591 | 5723 | 5843 | 5962 | 6066 | 6134 | 6177 | 6216 | 6251 | 6284 | 6314
| 11.5 | 5170 | 5313 | 5456 | 5599 | 5742 | 5880 | 6006 | 6129 | 6227 | 6326 | 6410 | 6464 | 6494 | 6522 | 6548 | 6571 | 6593
| 12 | 5524 | 5676 | 5829 | 5975 | 6106 | 6228 | 6332 | 6434 | 6514 | 6594 | 6660 | 6700 | 6721 | 6740 | 6758 | 6774 | 6789
| 12.5 | 5863 | 6020 | 6156 | 6284 | 6393 | 6495 | 6579 | 6662 | 6723 | 6784 | 6832 | 6859 | 6873 | 6885 | 6896 | 6906 | 6916
| 13 | 6166 | 6303 | 6417 | 6524 | 6613 | 6695 | 6760 | 6823 | 6866 | 6909 | 6940 | 6954 | 6961 | 6968 | 6973 | 6979 | 6983
| 13.5 | 6410 | 6526 | 6619 | 6705 | 6775 | 6837 | 6884 | 6928 | 6953 | 6979 | 6992 | 6995 | 6996 | 6997 | 6998 | 6999 | 7000
| 14 | 6603 | 6698 | 6771 | 6837 | 6888 | 6931 | 6960 | 6986 | 6993 | 6999 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000
| 14.5 | 6753 | 6827 | 6881 | 6928 | 6960 | 6984 | 6994 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000
| 15 | 6863 | 6917 | 6953 | 6981 | 6993 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000
| 15.5 | 6938 | 6974 | 6990 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000
| 16 | 6982 | 6999 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000
| 16.5 | 6999 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000
| 17 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000
| 17.5 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000
| 18 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000
| 18.5 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000
| 19 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000
| 19.5 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000
| 20 | 6882 | 6882 | 6882 | 6882 | 6882 | 6882 | 6882 | 6882 | 6882 | 6882 | 6882 | 6882 | 6882 | 6882 | 6882 | 6882 | 6882
| 20.5 | 6603 | 6603 | 6603 | 6603 | 6603 | 6603 | 6603 | 6603 | 6603 | 6603 | 6603 | 6603 | 6603 | 6603 | 6603 | 6603 | 6603
| 21 | 6331 | 6331 | 6331 | 6331 | 6331 | 6331 | 6331 | 6331 | 6331 | 6331 | 6331 | 6331 | 6331 | 6331 | 6331 | 6331 | 6331
| 21.5 | 6059 | 6059 | 6059 | 6059 | 6059 | 6059 | 6059 | 6059 | 6059 | 6059 | 6059 | 6059 | 6059 | 6059 | 6059 | 6059 | 6059
| 22 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794
| 22.5 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528
| 23 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 23.5 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012
| 24 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760
| 24.5 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508
| 25 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264
| 25.5 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019
| 26 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872
| 3.5 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86
| 4 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845
| 4.5 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831
| 5 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82
| 5.5 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813
| 6 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808
| 6.5 | 0.805 | 0.805 | 0.805 | 0.805 | 0.805 | 0.805 | 0.805 | 0.805 | 0.805 | 0.805 | 0.805 | 0.805 | 0.805 | 0.805 | 0.805 | 0.805 | 0.805
| 7 | 0.803 | 0.803 | 0.803 | 0.803 | 0.803 | 0.803 | 0.803 | 0.803 | 0.803 | 0.803 | 0.803 | 0.803 | 0.803 | 0.803 | 0.804 | 0.803 | 0.803
| 7.5 | 0.802 | 0.802 | 0.802 | 0.802 | 0.802 | 0.802 | 0.802 | 0.802 | 0.802 | 0.802 | 0.802 | 0.802 | 0.801 | 0.801 | 0.8 | 0.798 | 0.795
| 8 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.792 | 0.791 | 0.788 | 0.785 | 0.783 | 0.778 | 0.774
| 8.5 | 0.771 | 0.771 | 0.771 | 0.771 | 0.771 | 0.771 | 0.771 | 0.771 | 0.771 | 0.771 | 0.771 | 0.769 | 0.765 | 0.76 | 0.756 | 0.75 | 0.744
| 9 | 0.743 | 0.743 | 0.743 | 0.743 | 0.743 | 0.743 | 0.743 | 0.743 | 0.743 | 0.743 | 0.743 | 0.74 | 0.734 | 0.728 | 0.723 | 0.716 | 0.709
| 9.5 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.709 | 0.706 | 0.699 | 0.692 | 0.685 | 0.677 | 0.67
| 10 | 0.673 | 0.673 | 0.673 | 0.673 | 0.673 | 0.673 | 0.673 | 0.673 | 0.672 | 0.672 | 0.67 | 0.665 | 0.657 | 0.649 | 0.641 | 0.633 | 0.625
| 10.5 | 0.635 | 0.635 | 0.635 | 0.635 | 0.635 | 0.634 | 0.633 | 0.632 | 0.63 | 0.628 | 0.626 | 0.62 | 0.611 | 0.603 | 0.595 | 0.586 | 0.577
| 11 | 0.596 | 0.596 | 0.596 | 0.595 | 0.594 | 0.592 | 0.59 | 0.588 | 0.585 | 0.583 | 0.579 | 0.573 | 0.564 | 0.555 | 0.547 | 0.538 | 0.529
| 11.5 | 0.556 | 0.556 | 0.555 | 0.553 | 0.551 | 0.549 | 0.546 | 0.543 | 0.54 | 0.536 | 0.532 | 0.526 | 0.517 | 0.508 | 0.499 | 0.49 | 0.481
| 12 | 0.516 | 0.514 | 0.512 | 0.51 | 0.507 | 0.504 | 0.501 | 0.498 | 0.494 | 0.49 | 0.486 | 0.479 | 0.47 | 0.461 | 0.452 | 0.443 | 0.434
| 12.5 | 0.475 | 0.473 | 0.47 | 0.467 | 0.464 | 0.461 | 0.457 | 0.453 | 0.449 | 0.445 | 0.44 | 0.434 | 0.424 | 0.415 | 0.407 | 0.398 | 0.391
| 13 | 0.436 | 0.433 | 0.43 | 0.427 | 0.423 | 0.419 | 0.415 | 0.411 | 0.407 | 0.402 | 0.398 | 0.391 | 0.382 | 0.374 | 0.366 | 0.359 | 0.352
| 13.5 | 0.399 | 0.396 | 0.393 | 0.389 | 0.385 | 0.381 | 0.377 | 0.373 | 0.368 | 0.363 | 0.359 | 0.352 | 0.344 | 0.337 | 0.33 | 0.323 | 0.317
| 14 | 0.366 | 0.363 | 0.359 | 0.355 | 0.351 | 0.347 | 0.342 | 0.338 | 0.333 | 0.329 | 0.324 | 0.317 | 0.31 | 0.304 | 0.298 | 0.291 | 0.286
| 14.5 | 0.336 | 0.332 | 0.328 | 0.324 | 0.32 | 0.316 | 0.311 | 0.307 | 0.302 | 0.297 | 0.292 | 0.286 | 0.28 | 0.274 | 0.268 | 0.263 | 0.258
| 15 | 0.309 | 0.305 | 0.301 | 0.296 | 0.292 | 0.288 | 0.283 | 0.278 | 0.273 | 0.269 | 0.264 | 0.258 | 0.253 | 0.247 | 0.242 | 0.237 | 0.232
| 15.5 | 0.284 | 0.28 | 0.275 | 0.271 | 0.267 | 0.262 | 0.257 | 0.253 | 0.248 | 0.243 | 0.238 | 0.233 | 0.228 | 0.223 | 0.218 | 0.214 | 0.21
| 16 | 0.261 | 0.257 | 0.252 | 0.248 | 0.244 | 0.239 | 0.234 | 0.23 | 0.225 | 0.22 | 0.215 | 0.21 | 0.206 | 0.201 | 0.197 | 0.193 | 0.189
| 16.5 | 0.241 | 0.237 | 0.232 | 0.228 | 0.223 | 0.219 | 0.214 | 0.209 | 0.204 | 0.199 | 0.195 | 0.191 | 0.187 | 0.183 | 0.179 | 0.176 | 0.172
| 17 | 0.223 | 0.219 | 0.214 | 0.21 | 0.205 | 0.2 | 0.196 | 0.191 | 0.187 | 0.182 | 0.178 | 0.174 | 0.171 | 0.167 | 0.164 | 0.161 | 0.158
| 17.5 | 0.207 | 0.203 | 0.198 | 0.194 | 0.189 | 0.185 | 0.18 | 0.176 | 0.172 | 0.168 | 0.164 | 0.161 | 0.157 | 0.154 | 0.151 | 0.148 | 0.146
| 18 | 0.194 | 0.189 | 0.185 | 0.18 | 0.175 | 0.171 | 0.167 | 0.163 | 0.159 | 0.156 | 0.152 | 0.149 | 0.146 | 0.143 | 0.141 | 0.138 | 0.135
| 18.5 | 0.181 | 0.177 | 0.172 | 0.168 | 0.163 | 0.159 | 0.156 | 0.152 | 0.149 | 0.146 | 0.142 | 0.14 | 0.137 | 0.134 | 0.132 | 0.129 | 0.127
| 19 | 0.171 | 0.166 | 0.162 | 0.157 | 0.154 | 0.15 | 0.146 | 0.143 | 0.14 | 0.137 | 0.134 | 0.131 | 0.129 | 0.126 | 0.124 | 0.122 | 0.119
| 19.5 | 0.161 | 0.157 | 0.153 | 0.149 | 0.145 | 0.142 | 0.138 | 0.135 | 0.132 | 0.13 | 0.127 | 0.124 | 0.122 | 0.12 | 0.117 | 0.115 | 0.113
| 20 | 0.152 | 0.148 | 0.144 | 0.14 | 0.137 | 0.134 | 0.131 | 0.128 | 0.125 | 0.122 | 0.12 | 0.117 | 0.115 | 0.113 | 0.111 | 0.109 | 0.107
| 20.5 | 0.138 | 0.134 | 0.13 | 0.127 | 0.124 | 0.121 | 0.119 | 0.116 | 0.113 | 0.111 | 0.109 | 0.106 | 0.104 | 0.102 | 0.101 | 0.099 | 0.097
| 21 | 0.124 | 0.121 | 0.117 | 0.114 | 0.112 | 0.109 | 0.107 | 0.104 | 0.102 | 0.1 | 0.098 | 0.096 | 0.094 | 0.092 | 0.091 | 0.089 | 0.087
| 21.5 | 0.112 | 0.109 | 0.106 | 0.103 | 0.101 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083 | 0.082 | 0.08 | 0.079
| 22 | 0.1 | 0.097 | 0.095 | 0.092 | 0.09 | 0.088 | 0.086 | 0.084 | 0.082 | 0.08 | 0.079 | 0.077 | 0.076 | 0.075 | 0.073 | 0.072 | 0.071
| 22.5 | 0.09 | 0.087 | 0.085 | 0.083 | 0.081 | 0.079 | 0.077 | 0.076 | 0.074 | 0.072 | 0.071 | 0.069 | 0.068 | 0.067 | 0.066 | 0.064 | 0.063
| 23 | 0.08 | 0.078 | 0.076 | 0.074 | 0.072 | 0.071 | 0.069 | 0.068 | 0.066 | 0.064 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057
| 23.5 | 0.072 | 0.07 | 0.068 | 0.066 | 0.065 | 0.063 | 0.062 | 0.061 | 0.059 | 0.058 | 0.057 | 0.055 | 0.054 | 0.053 | 0.053 | 0.052 | 0.051
| 24 | 0.064 | 0.063 | 0.061 | 0.059 | 0.058 | 0.057 | 0.056 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045
| 24.5 | 0.058 | 0.056 | 0.055 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.042 | 0.041
| 25 | 0.053 | 0.051 | 0.05 | 0.049 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.038 | 0.037
| 25.5 | 0.048 | 0.047 | 0.046 | 0.044 | 0.043 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034
| 26 | 0.045 | 0.044 | 0.043 | 0.041 | 0.041 | 0.04 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032 | 0.032