## Sheet1
PROPERTIES
General
Name | N163-6.X MW 50-60 Hz vM12_4520
Manufacturer | Nordex
Hub Height | 118 | 138 | 148 | 158.5 | 164
Power
Rated Power | 4520
Peak Power | 4520
Power Regulation Type | Pitch
Voltage | 920
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | -
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -40
Low Temperature Restart | -20
High Temperature Shutdown | 40
High Temperature Restart | 50
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 39.5
Design TI | 0.35

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 22 | 24 | 26 | 28 | 30 | 32 | 34 | 37 | 39
| 3.5 | 114 | 118 | 122 | 127 | 131 | 135 | 139 | 143 | 147
| 4 | 239 | 246 | 253 | 260 | 267 | 274 | 281 | 288 | 295
| 4.5 | 396 | 406 | 417 | 427 | 438 | 448 | 459 | 469 | 480
| 5 | 583 | 598 | 613 | 628 | 643 | 657 | 672 | 687 | 702
| 5.5 | 806 | 826 | 845 | 865 | 885 | 905 | 925 | 944 | 964
| 6 | 1068 | 1093 | 1119 | 1145 | 1171 | 1196 | 1222 | 1248 | 1274
| 6.5 | 1363 | 1395 | 1428 | 1460 | 1492 | 1525 | 1557 | 1589 | 1622
| 7 | 1662 | 1701 | 1740 | 1779 | 1818 | 1858 | 1897 | 1936 | 1975
| 7.5 | 1948 | 1994 | 2040 | 2085 | 2131 | 2176 | 2222 | 2267 | 2313
| 8 | 2210 | 2262 | 2313 | 2364 | 2416 | 2467 | 2518 | 2570 | 2621
| 8.5 | 2447 | 2503 | 2560 | 2617 | 2673 | 2730 | 2787 | 2843 | 2900
| 9 | 2668 | 2730 | 2792 | 2853 | 2915 | 2976 | 3038 | 3100 | 3161
| 9.5 | 2882 | 2948 | 3015 | 3081 | 3148 | 3214 | 3280 | 3347 | 3413
| 10 | 3089 | 3160 | 3231 | 3302 | 3373 | 3444 | 3515 | 3585 | 3656
| 10.5 | 3285 | 3360 | 3436 | 3511 | 3586 | 3661 | 3737 | 3813 | 3888
| 11 | 3474 | 3554 | 3633 | 3713 | 3792 | 3873 | 3950 | 4022 | 4091
| 11.5 | 3659 | 3742 | 3826 | 3911 | 3989 | 4063 | 4131 | 4190 | 4246
| 12 | 3841 | 3929 | 4010 | 4086 | 4154 | 4215 | 4270 | 4317 | 4361
| 12.5 | 4015 | 4092 | 4161 | 4224 | 4279 | 4329 | 4372 | 4408 | 4441
| 13 | 4157 | 4221 | 4278 | 4329 | 4373 | 4410 | 4443 | 4467 | 4490
| 13.5 | 4271 | 4324 | 4369 | 4408 | 4441 | 4467 | 4489 | 4503 | 4516
| 14 | 4362 | 4403 | 4437 | 4465 | 4487 | 4503 | 4514 | 4518 | 4520
| 14.5 | 4430 | 4461 | 4484 | 4502 | 4513 | 4518 | 4520 | 4520 | 4520
| 15 | 4479 | 4498 | 4511 | 4518 | 4520 | 4520 | 4520 | 4520 | 4520
| 15.5 | 4508 | 4517 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 16 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 16.5 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 17 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 17.5 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 18 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 18.5 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 19 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 19.5 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 20 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 20.5 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 21 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 21.5 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 22 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 22.5 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 23 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 23.5 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 24 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 24.5 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508
| 25 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264
| 25.5 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019
| 26 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872
| 3.5 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86
| 4 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845
| 4.5 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831
| 5 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82
| 5.5 | 0.811 | 0.811 | 0.811 | 0.811 | 0.811 | 0.811 | 0.811 | 0.811 | 0.811
| 6 | 0.785 | 0.785 | 0.785 | 0.785 | 0.785 | 0.785 | 0.785 | 0.785 | 0.785
| 6.5 | 0.744 | 0.744 | 0.744 | 0.744 | 0.744 | 0.744 | 0.744 | 0.744 | 0.744
| 7 | 0.695 | 0.695 | 0.695 | 0.695 | 0.695 | 0.695 | 0.695 | 0.695 | 0.695
| 7.5 | 0.642 | 0.642 | 0.642 | 0.642 | 0.642 | 0.642 | 0.642 | 0.642 | 0.642
| 8 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588 | 0.588
| 8.5 | 0.534 | 0.534 | 0.534 | 0.534 | 0.534 | 0.534 | 0.534 | 0.534 | 0.534
| 9 | 0.481 | 0.481 | 0.481 | 0.481 | 0.481 | 0.481 | 0.481 | 0.481 | 0.481
| 9.5 | 0.432 | 0.432 | 0.432 | 0.432 | 0.432 | 0.432 | 0.432 | 0.432 | 0.432
| 10 | 0.389 | 0.389 | 0.389 | 0.389 | 0.389 | 0.389 | 0.388 | 0.388 | 0.388
| 10.5 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352 | 0.351 | 0.351 | 0.35 | 0.349
| 11 | 0.32 | 0.32 | 0.32 | 0.319 | 0.318 | 0.318 | 0.317 | 0.315 | 0.314
| 11.5 | 0.292 | 0.291 | 0.291 | 0.29 | 0.289 | 0.288 | 0.286 | 0.285 | 0.283
| 12 | 0.267 | 0.266 | 0.265 | 0.264 | 0.262 | 0.261 | 0.259 | 0.258 | 0.256
| 12.5 | 0.244 | 0.243 | 0.242 | 0.24 | 0.239 | 0.237 | 0.235 | 0.234 | 0.232
| 13 | 0.223 | 0.222 | 0.221 | 0.219 | 0.217 | 0.216 | 0.214 | 0.212 | 0.21
| 13.5 | 0.205 | 0.203 | 0.202 | 0.2 | 0.198 | 0.197 | 0.195 | 0.193 | 0.191
| 14 | 0.188 | 0.187 | 0.185 | 0.183 | 0.181 | 0.179 | 0.177 | 0.175 | 0.173
| 14.5 | 0.173 | 0.171 | 0.169 | 0.168 | 0.166 | 0.164 | 0.162 | 0.16 | 0.157
| 15 | 0.159 | 0.157 | 0.155 | 0.153 | 0.151 | 0.149 | 0.147 | 0.145 | 0.143
| 15.5 | 0.146 | 0.144 | 0.143 | 0.141 | 0.139 | 0.137 | 0.135 | 0.132 | 0.13
| 16 | 0.135 | 0.133 | 0.131 | 0.129 | 0.127 | 0.125 | 0.123 | 0.121 | 0.119
| 16.5 | 0.125 | 0.123 | 0.121 | 0.119 | 0.117 | 0.115 | 0.113 | 0.111 | 0.108
| 17 | 0.116 | 0.114 | 0.112 | 0.11 | 0.108 | 0.106 | 0.104 | 0.102 | 0.1
| 17.5 | 0.108 | 0.106 | 0.104 | 0.102 | 0.1 | 0.098 | 0.096 | 0.094 | 0.093
| 18 | 0.101 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.09 | 0.088 | 0.086
| 18.5 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084 | 0.082 | 0.081
| 19 | 0.09 | 0.088 | 0.086 | 0.084 | 0.082 | 0.081 | 0.079 | 0.078 | 0.076
| 19.5 | 0.085 | 0.083 | 0.081 | 0.08 | 0.078 | 0.077 | 0.075 | 0.074 | 0.073
| 20 | 0.081 | 0.079 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.071 | 0.069
| 20.5 | 0.073 | 0.071 | 0.07 | 0.068 | 0.067 | 0.066 | 0.065 | 0.064 | 0.062
| 21 | 0.066 | 0.064 | 0.063 | 0.062 | 0.061 | 0.059 | 0.058 | 0.058 | 0.056
| 21.5 | 0.059 | 0.058 | 0.057 | 0.055 | 0.055 | 0.053 | 0.052 | 0.052 | 0.05
| 22 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045
| 22.5 | 0.047 | 0.046 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.042 | 0.04
| 23 | 0.042 | 0.041 | 0.041 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037 | 0.036
| 23.5 | 0.038 | 0.037 | 0.037 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032
| 24 | 0.034 | 0.033 | 0.033 | 0.032 | 0.032 | 0.031 | 0.03 | 0.03 | 0.029
| 24.5 | 0.031 | 0.03 | 0.03 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026
| 25 | 0.028 | 0.027 | 0.027 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024
| 25.5 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022
| 26 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.02