## Sheet1
PROPERTIES
General
Name | N163-6.X MW 50-60 Hz vM14_3870
Manufacturer | Nordex
Hub Height | 118 | 138 | 148 | 158.5 | 164
Power
Rated Power | 3870
Peak Power | 3870
Power Regulation Type | Pitch
Voltage | 920
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | -
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -40
Low Temperature Restart | -20
High Temperature Shutdown | 40
High Temperature Restart | 50
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 39.5
Design TI | 0.35

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 22 | 24 | 26 | 28 | 30 | 32 | 34 | 37 | 39
| 3.5 | 114 | 118 | 122 | 127 | 131 | 135 | 139 | 143 | 147
| 4 | 239 | 246 | 253 | 260 | 267 | 274 | 281 | 288 | 295
| 4.5 | 396 | 406 | 417 | 427 | 438 | 448 | 459 | 469 | 480
| 5 | 583 | 598 | 613 | 628 | 643 | 657 | 672 | 687 | 702
| 5.5 | 806 | 826 | 845 | 865 | 885 | 905 | 925 | 945 | 964
| 6 | 1065 | 1090 | 1116 | 1142 | 1167 | 1193 | 1219 | 1244 | 1270
| 6.5 | 1339 | 1371 | 1402 | 1434 | 1466 | 1498 | 1530 | 1562 | 1593
| 7 | 1606 | 1644 | 1681 | 1719 | 1757 | 1795 | 1833 | 1871 | 1908
| 7.5 | 1852 | 1896 | 1939 | 1982 | 2026 | 2069 | 2112 | 2156 | 2199
| 8 | 2074 | 2122 | 2170 | 2219 | 2267 | 2315 | 2364 | 2412 | 2460
| 8.5 | 2278 | 2331 | 2384 | 2437 | 2490 | 2543 | 2596 | 2649 | 2702
| 9 | 2474 | 2532 | 2589 | 2646 | 2704 | 2761 | 2818 | 2876 | 2933
| 9.5 | 2664 | 2726 | 2788 | 2849 | 2911 | 2972 | 3034 | 3095 | 3157
| 10 | 2844 | 2910 | 2975 | 3041 | 3106 | 3172 | 3238 | 3303 | 3365
| 10.5 | 3017 | 3087 | 3156 | 3226 | 3296 | 3363 | 3428 | 3490 | 3540
| 11 | 3186 | 3260 | 3334 | 3403 | 3469 | 3529 | 3581 | 3631 | 3671
| 11.5 | 3353 | 3424 | 3492 | 3551 | 3606 | 3654 | 3695 | 3735 | 3764
| 12 | 3500 | 3560 | 3616 | 3664 | 3707 | 3745 | 3776 | 3805 | 3825
| 12.5 | 3616 | 3664 | 3709 | 3747 | 3779 | 3807 | 3828 | 3847 | 3857
| 13 | 3707 | 3745 | 3779 | 3806 | 3829 | 3847 | 3858 | 3868 | 3869
| 13.5 | 3776 | 3804 | 3828 | 3845 | 3859 | 3867 | 3869 | 3870 | 3870
| 14 | 3825 | 3843 | 3858 | 3866 | 3869 | 3870 | 3870 | 3870 | 3870
| 14.5 | 3856 | 3864 | 3869 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870
| 15 | 3869 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870
| 15.5 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870
| 16 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870
| 16.5 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870
| 17 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870
| 17.5 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870
| 18 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870
| 18.5 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870
| 19 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870
| 19.5 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870
| 20 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870
| 20.5 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870
| 21 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870
| 21.5 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870
| 22 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870
| 22.5 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870
| 23 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870
| 23.5 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870
| 24 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870
| 24.5 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870
| 25 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870
| 25.5 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870 | 3870
| 26 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872
| 3.5 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86
| 4 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845
| 4.5 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831
| 5 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82
| 5.5 | 0.802 | 0.802 | 0.802 | 0.802 | 0.802 | 0.802 | 0.802 | 0.802 | 0.802
| 6 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764
| 6.5 | 0.715 | 0.715 | 0.715 | 0.715 | 0.715 | 0.715 | 0.715 | 0.715 | 0.715
| 7 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66
| 7.5 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603
| 8 | 0.546 | 0.546 | 0.546 | 0.546 | 0.546 | 0.546 | 0.546 | 0.546 | 0.546
| 8.5 | 0.491 | 0.491 | 0.491 | 0.491 | 0.491 | 0.491 | 0.491 | 0.491 | 0.491
| 9 | 0.438 | 0.438 | 0.438 | 0.438 | 0.438 | 0.438 | 0.438 | 0.438 | 0.438
| 9.5 | 0.392 | 0.392 | 0.392 | 0.392 | 0.392 | 0.392 | 0.392 | 0.392 | 0.391
| 10 | 0.353 | 0.353 | 0.353 | 0.353 | 0.353 | 0.352 | 0.352 | 0.351 | 0.349
| 10.5 | 0.32 | 0.32 | 0.319 | 0.318 | 0.318 | 0.317 | 0.316 | 0.314 | 0.313
| 11 | 0.29 | 0.289 | 0.289 | 0.288 | 0.286 | 0.285 | 0.284 | 0.282 | 0.28
| 11.5 | 0.264 | 0.263 | 0.261 | 0.26 | 0.259 | 0.257 | 0.255 | 0.254 | 0.252
| 12 | 0.24 | 0.239 | 0.237 | 0.236 | 0.234 | 0.232 | 0.23 | 0.229 | 0.226
| 12.5 | 0.219 | 0.217 | 0.216 | 0.214 | 0.212 | 0.21 | 0.208 | 0.206 | 0.204
| 13 | 0.199 | 0.198 | 0.196 | 0.194 | 0.192 | 0.19 | 0.188 | 0.186 | 0.184
| 13.5 | 0.182 | 0.18 | 0.179 | 0.177 | 0.175 | 0.173 | 0.171 | 0.168 | 0.166
| 14 | 0.167 | 0.165 | 0.163 | 0.161 | 0.159 | 0.157 | 0.155 | 0.152 | 0.15
| 14.5 | 0.152 | 0.15 | 0.149 | 0.146 | 0.144 | 0.142 | 0.14 | 0.138 | 0.136
| 15 | 0.14 | 0.138 | 0.136 | 0.134 | 0.132 | 0.129 | 0.127 | 0.125 | 0.123
| 15.5 | 0.128 | 0.126 | 0.124 | 0.122 | 0.12 | 0.118 | 0.116 | 0.113 | 0.111
| 16 | 0.118 | 0.116 | 0.114 | 0.112 | 0.109 | 0.107 | 0.105 | 0.103 | 0.101
| 16.5 | 0.108 | 0.106 | 0.104 | 0.102 | 0.1 | 0.098 | 0.096 | 0.094 | 0.093
| 17 | 0.1 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.089 | 0.087 | 0.086
| 17.5 | 0.093 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084 | 0.082 | 0.081 | 0.079
| 18 | 0.087 | 0.085 | 0.083 | 0.081 | 0.08 | 0.078 | 0.077 | 0.075 | 0.074
| 18.5 | 0.081 | 0.08 | 0.078 | 0.076 | 0.075 | 0.074 | 0.072 | 0.071 | 0.07
| 19 | 0.077 | 0.075 | 0.074 | 0.072 | 0.071 | 0.07 | 0.068 | 0.067 | 0.066
| 19.5 | 0.073 | 0.071 | 0.07 | 0.069 | 0.067 | 0.066 | 0.065 | 0.064 | 0.063
| 20 | 0.07 | 0.068 | 0.067 | 0.066 | 0.064 | 0.063 | 0.062 | 0.061 | 0.06
| 20.5 | 0.063 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054
| 21 | 0.057 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.049
| 21.5 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.044
| 22 | 0.046 | 0.044 | 0.044 | 0.043 | 0.042 | 0.041 | 0.041 | 0.04 | 0.039
| 22.5 | 0.041 | 0.04 | 0.039 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035
| 23 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.033 | 0.032 | 0.032 | 0.031
| 23.5 | 0.033 | 0.032 | 0.031 | 0.031 | 0.03 | 0.03 | 0.029 | 0.029 | 0.028
| 24 | 0.029 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.026 | 0.025
| 24.5 | 0.027 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.023 | 0.023 | 0.023
| 25 | 0.024 | 0.023 | 0.023 | 0.023 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021
| 25.5 | 0.022 | 0.021 | 0.021 | 0.021 | 0.02 | 0.02 | 0.02 | 0.019 | 0.019
| 26 | 0.021 | 0.02 | 0.02 | 0.019 | 0.019 | 0.019 | 0.018 | 0.018 | 0.018