## Sheet1
PROPERTIES
General
Name | N163-6.X MW 50-60 Hz vM15_3620
Manufacturer | Nordex
Hub Height | 118 | 138 | 148 | 158.5 | 164
Power
Rated Power | 3620
Peak Power | 3620
Power Regulation Type | Pitch
Voltage | 920
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | -
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -40
Low Temperature Restart | -20
High Temperature Shutdown | 40
High Temperature Restart | 50
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 39.5
Design TI | 0.35

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 22 | 24 | 26 | 28 | 30 | 32 | 34 | 37 | 39
| 3.5 | 114 | 118 | 122 | 127 | 131 | 135 | 139 | 143 | 147
| 4 | 239 | 246 | 253 | 260 | 267 | 274 | 281 | 288 | 295
| 4.5 | 396 | 406 | 417 | 427 | 438 | 448 | 459 | 469 | 480
| 5 | 583 | 598 | 613 | 628 | 643 | 657 | 672 | 687 | 702
| 5.5 | 806 | 826 | 845 | 865 | 885 | 905 | 925 | 945 | 964
| 6 | 1061 | 1086 | 1112 | 1137 | 1163 | 1189 | 1214 | 1240 | 1265
| 6.5 | 1322 | 1354 | 1385 | 1417 | 1448 | 1479 | 1511 | 1542 | 1574
| 7 | 1572 | 1609 | 1646 | 1683 | 1720 | 1757 | 1794 | 1831 | 1869
| 7.5 | 1799 | 1841 | 1883 | 1925 | 1967 | 2010 | 2052 | 2094 | 2136
| 8 | 2003 | 2050 | 2097 | 2143 | 2190 | 2237 | 2284 | 2330 | 2377
| 8.5 | 2195 | 2246 | 2297 | 2348 | 2399 | 2450 | 2501 | 2552 | 2603
| 9 | 2380 | 2435 | 2490 | 2546 | 2601 | 2656 | 2711 | 2766 | 2821
| 9.5 | 2557 | 2616 | 2675 | 2734 | 2793 | 2852 | 2911 | 2971 | 3030
| 10 | 2725 | 2788 | 2851 | 2914 | 2977 | 3040 | 3103 | 3162 | 3222
| 10.5 | 2888 | 2955 | 3022 | 3089 | 3153 | 3215 | 3273 | 3322 | 3370
| 11 | 3049 | 3120 | 3185 | 3249 | 3305 | 3355 | 3402 | 3441 | 3479
| 11.5 | 3201 | 3267 | 3322 | 3374 | 3419 | 3459 | 3496 | 3524 | 3553
| 12 | 3328 | 3381 | 3426 | 3468 | 3503 | 3533 | 3559 | 3578 | 3597
| 12.5 | 3426 | 3470 | 3504 | 3536 | 3561 | 3581 | 3599 | 3608 | 3618
| 13 | 3503 | 3536 | 3561 | 3582 | 3598 | 3610 | 3618 | 3619 | 3620
| 13.5 | 3558 | 3582 | 3597 | 3610 | 3617 | 3619 | 3620 | 3620 | 3620
| 14 | 3595 | 3610 | 3616 | 3619 | 3620 | 3620 | 3620 | 3620 | 3620
| 14.5 | 3615 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620
| 15 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620
| 15.5 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620
| 16 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620
| 16.5 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620
| 17 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620
| 17.5 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620
| 18 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620
| 18.5 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620
| 19 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620
| 19.5 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620
| 20 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620 | 3620

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872
| 3.5 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86
| 4 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845
| 4.5 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831
| 5 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82
| 5.5 | 0.796 | 0.796 | 0.796 | 0.796 | 0.796 | 0.796 | 0.796 | 0.796 | 0.796
| 6 | 0.753 | 0.753 | 0.753 | 0.753 | 0.753 | 0.753 | 0.753 | 0.753 | 0.753
| 6.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
| 7 | 0.642 | 0.642 | 0.642 | 0.642 | 0.642 | 0.642 | 0.642 | 0.642 | 0.642
| 7.5 | 0.583 | 0.583 | 0.583 | 0.583 | 0.583 | 0.583 | 0.583 | 0.583 | 0.583
| 8 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525 | 0.525
| 8.5 | 0.469 | 0.469 | 0.469 | 0.469 | 0.469 | 0.469 | 0.469 | 0.469 | 0.469
| 9 | 0.418 | 0.418 | 0.418 | 0.418 | 0.418 | 0.418 | 0.418 | 0.418 | 0.418
| 9.5 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.373 | 0.373 | 0.372
| 10 | 0.337 | 0.337 | 0.337 | 0.337 | 0.336 | 0.335 | 0.334 | 0.333 | 0.332
| 10.5 | 0.305 | 0.304 | 0.304 | 0.303 | 0.302 | 0.301 | 0.3 | 0.298 | 0.297
| 11 | 0.276 | 0.275 | 0.274 | 0.273 | 0.272 | 0.271 | 0.269 | 0.268 | 0.266
| 11.5 | 0.251 | 0.25 | 0.248 | 0.247 | 0.245 | 0.244 | 0.242 | 0.24 | 0.239
| 12 | 0.228 | 0.227 | 0.225 | 0.224 | 0.222 | 0.22 | 0.218 | 0.216 | 0.214
| 12.5 | 0.208 | 0.206 | 0.204 | 0.203 | 0.201 | 0.199 | 0.197 | 0.195 | 0.193
| 13 | 0.189 | 0.188 | 0.186 | 0.184 | 0.182 | 0.18 | 0.178 | 0.176 | 0.174
| 13.5 | 0.173 | 0.171 | 0.169 | 0.167 | 0.165 | 0.163 | 0.161 | 0.159 | 0.157
| 14 | 0.158 | 0.156 | 0.154 | 0.152 | 0.15 | 0.148 | 0.146 | 0.144 | 0.141
| 14.5 | 0.144 | 0.142 | 0.14 | 0.138 | 0.136 | 0.134 | 0.132 | 0.13 | 0.128
| 15 | 0.132 | 0.13 | 0.128 | 0.126 | 0.124 | 0.122 | 0.12 | 0.118 | 0.115
| 15.5 | 0.121 | 0.119 | 0.117 | 0.115 | 0.113 | 0.111 | 0.109 | 0.107 | 0.105
| 16 | 0.111 | 0.109 | 0.107 | 0.105 | 0.103 | 0.101 | 0.099 | 0.097 | 0.095
| 16.5 | 0.102 | 0.1 | 0.098 | 0.096 | 0.094 | 0.092 | 0.091 | 0.089 | 0.087
| 17 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.085 | 0.084 | 0.082 | 0.081
| 17.5 | 0.088 | 0.086 | 0.084 | 0.082 | 0.081 | 0.079 | 0.078 | 0.076 | 0.075
| 18 | 0.082 | 0.08 | 0.078 | 0.077 | 0.075 | 0.074 | 0.072 | 0.071 | 0.07
| 18.5 | 0.077 | 0.075 | 0.074 | 0.072 | 0.071 | 0.069 | 0.068 | 0.067 | 0.066
| 19 | 0.072 | 0.071 | 0.07 | 0.068 | 0.067 | 0.066 | 0.064 | 0.063 | 0.062
| 19.5 | 0.069 | 0.067 | 0.066 | 0.065 | 0.064 | 0.062 | 0.061 | 0.06 | 0.059
| 20 | 0.066 | 0.064 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057