## Sheet1
PROPERTIES
General
Name | N163-6.X MW 50-60 Hz vM16_3380
Manufacturer | Nordex
Hub Height | 118 | 138 | 148 | 158.5 | 164
Power
Rated Power | 3380
Peak Power | 3380
Power Regulation Type | Pitch
Voltage | 920
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | -
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -40
Low Temperature Restart | -20
High Temperature Shutdown | 40
High Temperature Restart | 50
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 39.5
Design TI | 0.35

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 22 | 24 | 26 | 28 | 30 | 32 | 35 | 37 | 39
| 3.5 | 114 | 118 | 122 | 127 | 131 | 135 | 139 | 143 | 147
| 4 | 239 | 246 | 253 | 260 | 267 | 274 | 281 | 288 | 295
| 4.5 | 396 | 406 | 417 | 427 | 438 | 448 | 459 | 469 | 480
| 5 | 583 | 598 | 613 | 628 | 643 | 657 | 672 | 687 | 702
| 5.5 | 805 | 825 | 845 | 865 | 885 | 905 | 924 | 944 | 964
| 6 | 1053 | 1079 | 1104 | 1130 | 1155 | 1181 | 1206 | 1231 | 1257
| 6.5 | 1301 | 1332 | 1363 | 1394 | 1425 | 1456 | 1487 | 1518 | 1549
| 7 | 1533 | 1569 | 1605 | 1642 | 1678 | 1714 | 1750 | 1786 | 1822
| 7.5 | 1741 | 1782 | 1823 | 1864 | 1905 | 1946 | 1986 | 2027 | 2068
| 8 | 1931 | 1976 | 2021 | 2066 | 2111 | 2156 | 2201 | 2247 | 2292
| 8.5 | 2111 | 2160 | 2209 | 2258 | 2307 | 2356 | 2406 | 2455 | 2504
| 9 | 2285 | 2338 | 2391 | 2445 | 2498 | 2551 | 2604 | 2657 | 2710
| 9.5 | 2450 | 2507 | 2564 | 2621 | 2677 | 2734 | 2791 | 2848 | 2903
| 10 | 2608 | 2669 | 2729 | 2789 | 2850 | 2910 | 2967 | 3024 | 3069
| 10.5 | 2762 | 2826 | 2891 | 2952 | 3011 | 3066 | 3112 | 3158 | 3194
| 11 | 2915 | 2978 | 3039 | 3091 | 3139 | 3183 | 3219 | 3256 | 3282
| 11.5 | 3051 | 3103 | 3153 | 3195 | 3233 | 3267 | 3294 | 3321 | 3338
| 12 | 3157 | 3199 | 3239 | 3271 | 3300 | 3324 | 3342 | 3360 | 3368
| 12.5 | 3240 | 3272 | 3303 | 3326 | 3345 | 3361 | 3370 | 3379 | 3380
| 13 | 3302 | 3325 | 3346 | 3361 | 3371 | 3378 | 3379 | 3380 | 3380
| 13.5 | 3346 | 3360 | 3372 | 3377 | 3379 | 3380 | 3380 | 3380 | 3380
| 14 | 3371 | 3377 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380
| 14.5 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380
| 15 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380
| 15.5 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380
| 16 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380
| 16.5 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380
| 17 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380
| 17.5 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380
| 18 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380
| 18.5 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380
| 19 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380
| 19.5 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380
| 20 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380 | 3380

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872
| 3.5 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86
| 4 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845
| 4.5 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831
| 5 | 0.819 | 0.819 | 0.819 | 0.819 | 0.819 | 0.819 | 0.819 | 0.819 | 0.819
| 5.5 | 0.788 | 0.788 | 0.788 | 0.788 | 0.788 | 0.788 | 0.788 | 0.788 | 0.788
| 6 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74
| 6.5 | 0.683 | 0.683 | 0.683 | 0.683 | 0.683 | 0.683 | 0.683 | 0.683 | 0.683
| 7 | 0.622 | 0.622 | 0.622 | 0.622 | 0.622 | 0.622 | 0.622 | 0.622 | 0.622
| 7.5 | 0.562 | 0.562 | 0.562 | 0.562 | 0.562 | 0.562 | 0.562 | 0.562 | 0.562
| 8 | 0.503 | 0.503 | 0.503 | 0.503 | 0.503 | 0.503 | 0.503 | 0.503 | 0.503
| 8.5 | 0.447 | 0.447 | 0.447 | 0.447 | 0.447 | 0.447 | 0.447 | 0.447 | 0.447
| 9 | 0.398 | 0.398 | 0.398 | 0.398 | 0.398 | 0.398 | 0.398 | 0.398 | 0.397
| 9.5 | 0.356 | 0.356 | 0.356 | 0.356 | 0.356 | 0.356 | 0.355 | 0.354 | 0.353
| 10 | 0.321 | 0.321 | 0.321 | 0.32 | 0.319 | 0.318 | 0.317 | 0.316 | 0.315
| 10.5 | 0.29 | 0.289 | 0.289 | 0.288 | 0.287 | 0.285 | 0.284 | 0.283 | 0.281
| 11 | 0.263 | 0.262 | 0.26 | 0.259 | 0.258 | 0.256 | 0.255 | 0.253 | 0.251
| 11.5 | 0.238 | 0.237 | 0.235 | 0.234 | 0.232 | 0.231 | 0.229 | 0.227 | 0.225
| 12 | 0.216 | 0.215 | 0.213 | 0.212 | 0.21 | 0.208 | 0.206 | 0.204 | 0.202
| 12.5 | 0.197 | 0.195 | 0.193 | 0.192 | 0.19 | 0.188 | 0.186 | 0.184 | 0.182
| 13 | 0.179 | 0.177 | 0.175 | 0.174 | 0.172 | 0.17 | 0.168 | 0.166 | 0.163
| 13.5 | 0.163 | 0.161 | 0.159 | 0.157 | 0.155 | 0.153 | 0.151 | 0.149 | 0.147
| 14 | 0.149 | 0.147 | 0.145 | 0.143 | 0.141 | 0.139 | 0.137 | 0.135 | 0.132
| 14.5 | 0.136 | 0.134 | 0.132 | 0.13 | 0.128 | 0.126 | 0.124 | 0.122 | 0.119
| 15 | 0.124 | 0.122 | 0.12 | 0.118 | 0.116 | 0.114 | 0.112 | 0.11 | 0.108
| 15.5 | 0.114 | 0.112 | 0.11 | 0.108 | 0.106 | 0.104 | 0.102 | 0.1 | 0.098
| 16 | 0.104 | 0.102 | 0.1 | 0.098 | 0.096 | 0.094 | 0.093 | 0.091 | 0.089
| 16.5 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.087 | 0.085 | 0.083 | 0.082
| 17 | 0.089 | 0.087 | 0.085 | 0.083 | 0.081 | 0.08 | 0.078 | 0.077 | 0.076
| 17.5 | 0.082 | 0.08 | 0.079 | 0.077 | 0.076 | 0.074 | 0.073 | 0.071 | 0.07
| 18 | 0.077 | 0.075 | 0.073 | 0.072 | 0.071 | 0.069 | 0.068 | 0.067 | 0.066
| 18.5 | 0.072 | 0.07 | 0.069 | 0.068 | 0.066 | 0.065 | 0.064 | 0.063 | 0.062
| 19 | 0.068 | 0.067 | 0.065 | 0.064 | 0.063 | 0.062 | 0.06 | 0.059 | 0.058
| 19.5 | 0.065 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056
| 20 | 0.062 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053