## Sheet1
PROPERTIES
General
Name | N163-6.X MW 50-60 Hz vM5_6240
Manufacturer | Nordex
Hub Height | 118 | 138 | 148 | 158.5 | 164
Power
Rated Power | 6240
Peak Power | 6240
Power Regulation Type | Pitch
Voltage | 920
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -40
Low Temperature Restart | -20
High Temperature Shutdown | 40
High Temperature Restart | 50
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 38.8
Design TI | 0.35

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 5 | 7 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 28 | 30 | 32 | 34 | 37 | 39
| 3.5 | 81 | 85 | 89 | 93 | 97 | 102 | 106 | 110 | 114 | 118 | 122 | 127 | 131 | 135 | 139 | 143 | 147
| 4 | 183 | 190 | 197 | 204 | 211 | 218 | 225 | 232 | 239 | 246 | 253 | 260 | 267 | 274 | 281 | 288 | 295
| 4.5 | 311 | 322 | 332 | 343 | 353 | 364 | 374 | 385 | 396 | 406 | 417 | 427 | 438 | 448 | 459 | 469 | 480
| 5 | 465 | 480 | 495 | 509 | 524 | 539 | 554 | 569 | 583 | 598 | 613 | 628 | 643 | 657 | 672 | 687 | 702
| 5.5 | 647 | 667 | 687 | 706 | 726 | 746 | 766 | 786 | 806 | 826 | 845 | 865 | 885 | 905 | 925 | 944 | 964
| 6 | 862 | 887 | 913 | 939 | 965 | 991 | 1016 | 1042 | 1068 | 1094 | 1119 | 1145 | 1171 | 1197 | 1222 | 1248 | 1274
| 6.5 | 1114 | 1146 | 1179 | 1212 | 1245 | 1277 | 1310 | 1343 | 1375 | 1408 | 1441 | 1473 | 1506 | 1539 | 1571 | 1604 | 1637
| 7 | 1407 | 1448 | 1488 | 1529 | 1570 | 1611 | 1651 | 1692 | 1733 | 1774 | 1814 | 1855 | 1896 | 1936 | 1977 | 2018 | 2058
| 7.5 | 1744 | 1795 | 1845 | 1895 | 1945 | 1995 | 2045 | 2095 | 2145 | 2195 | 2245 | 2294 | 2344 | 2394 | 2444 | 2494 | 2544
| 8 | 2121 | 2181 | 2242 | 2302 | 2362 | 2423 | 2483 | 2543 | 2604 | 2664 | 2724 | 2784 | 2844 | 2904 | 2965 | 3025 | 3085
| 8.5 | 2512 | 2583 | 2654 | 2725 | 2796 | 2867 | 2938 | 3009 | 3080 | 3151 | 3221 | 3292 | 3363 | 3434 | 3504 | 3575 | 3645
| 9 | 2897 | 2978 | 3060 | 3141 | 3223 | 3304 | 3386 | 3467 | 3548 | 3629 | 3711 | 3792 | 3873 | 3954 | 4035 | 4116 | 4197
| 9.5 | 3265 | 3356 | 3448 | 3539 | 3631 | 3722 | 3814 | 3905 | 3996 | 4087 | 4178 | 4270 | 4360 | 4451 | 4542 | 4634 | 4725
| 10 | 3607 | 3707 | 3808 | 3909 | 4010 | 4110 | 4211 | 4311 | 4412 | 4512 | 4612 | 4712 | 4813 | 4914 | 5014 | 5109 | 5204
| 10.5 | 3921 | 4031 | 4140 | 4249 | 4358 | 4467 | 4577 | 4685 | 4794 | 4903 | 5013 | 5123 | 5224 | 5325 | 5422 | 5500 | 5578
| 11 | 4216 | 4333 | 4450 | 4568 | 4685 | 4802 | 4918 | 5036 | 5154 | 5267 | 5372 | 5478 | 5562 | 5644 | 5724 | 5786 | 5848
| 11.5 | 4499 | 4624 | 4748 | 4873 | 4998 | 5123 | 5248 | 5364 | 5473 | 5574 | 5660 | 5747 | 5815 | 5881 | 5944 | 5991 | 6037
| 12 | 4774 | 4906 | 5039 | 5171 | 5303 | 5422 | 5536 | 5634 | 5725 | 5807 | 5877 | 5947 | 5999 | 6048 | 6096 | 6127 | 6158
| 12.5 | 5042 | 5182 | 5321 | 5449 | 5566 | 5667 | 5762 | 5842 | 5916 | 5981 | 6034 | 6088 | 6124 | 6158 | 6190 | 6205 | 6221
| 13 | 5299 | 5443 | 5568 | 5678 | 5776 | 5859 | 5936 | 6000 | 6056 | 6105 | 6142 | 6179 | 6200 | 6219 | 6235 | 6237 | 6239
| 13.5 | 5538 | 5663 | 5768 | 5860 | 5941 | 6006 | 6066 | 6113 | 6153 | 6186 | 6208 | 6230 | 6235 | 6238 | 6240 | 6240 | 6240
| 14 | 5735 | 5840 | 5928 | 6002 | 6065 | 6114 | 6157 | 6188 | 6213 | 6230 | 6236 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240
| 14.5 | 5894 | 5981 | 6051 | 6108 | 6154 | 6187 | 6214 | 6229 | 6237 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240
| 15 | 6018 | 6088 | 6140 | 6181 | 6211 | 6227 | 6238 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240
| 15.5 | 6111 | 6163 | 6199 | 6223 | 6237 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240
| 16 | 6175 | 6211 | 6231 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240
| 16.5 | 6216 | 6235 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240
| 17 | 6237 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240
| 17.5 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240
| 18 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240
| 18.5 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240
| 19 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240
| 19.5 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240
| 20 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240
| 20.5 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240
| 21 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240 | 6240
| 21.5 | 6059 | 6059 | 6059 | 6059 | 6059 | 6059 | 6059 | 6059 | 6059 | 6059 | 6059 | 6059 | 6059 | 6059 | 6059 | 6059 | 6059
| 22 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794
| 22.5 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528
| 23 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 23.5 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012
| 24 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760
| 24.5 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508
| 25 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264
| 25.5 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019
| 26 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872
| 3.5 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86
| 4 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845
| 4.5 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831
| 5 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82
| 5.5 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813
| 6 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808
| 6.5 | 0.805 | 0.805 | 0.805 | 0.805 | 0.805 | 0.805 | 0.805 | 0.805 | 0.805 | 0.805 | 0.805 | 0.805 | 0.805 | 0.805 | 0.805 | 0.805 | 0.805
| 7 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| 7.5 | 0.783 | 0.783 | 0.783 | 0.783 | 0.783 | 0.783 | 0.783 | 0.783 | 0.783 | 0.783 | 0.783 | 0.783 | 0.783 | 0.783 | 0.783 | 0.783 | 0.783
| 8 | 0.756 | 0.756 | 0.756 | 0.756 | 0.756 | 0.756 | 0.756 | 0.756 | 0.756 | 0.756 | 0.756 | 0.756 | 0.756 | 0.756 | 0.756 | 0.756 | 0.756
| 8.5 | 0.721 | 0.721 | 0.721 | 0.721 | 0.721 | 0.721 | 0.721 | 0.721 | 0.721 | 0.721 | 0.721 | 0.721 | 0.721 | 0.721 | 0.721 | 0.721 | 0.721
| 9 | 0.682 | 0.682 | 0.682 | 0.682 | 0.682 | 0.682 | 0.682 | 0.682 | 0.682 | 0.682 | 0.682 | 0.682 | 0.682 | 0.682 | 0.682 | 0.682 | 0.682
| 9.5 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.639 | 0.637 | 0.636
| 10 | 0.597 | 0.597 | 0.597 | 0.597 | 0.597 | 0.597 | 0.597 | 0.597 | 0.597 | 0.597 | 0.597 | 0.596 | 0.594 | 0.593 | 0.591 | 0.589 | 0.587
| 10.5 | 0.554 | 0.554 | 0.554 | 0.554 | 0.554 | 0.554 | 0.554 | 0.554 | 0.553 | 0.552 | 0.55 | 0.549 | 0.547 | 0.544 | 0.542 | 0.539 | 0.536
| 11 | 0.512 | 0.512 | 0.512 | 0.512 | 0.512 | 0.511 | 0.51 | 0.509 | 0.507 | 0.505 | 0.503 | 0.501 | 0.498 | 0.496 | 0.493 | 0.49 | 0.486
| 11.5 | 0.471 | 0.471 | 0.47 | 0.47 | 0.469 | 0.467 | 0.466 | 0.464 | 0.462 | 0.459 | 0.457 | 0.454 | 0.451 | 0.448 | 0.445 | 0.441 | 0.438
| 12 | 0.432 | 0.432 | 0.431 | 0.429 | 0.428 | 0.426 | 0.424 | 0.421 | 0.419 | 0.416 | 0.413 | 0.41 | 0.406 | 0.403 | 0.4 | 0.396 | 0.392
| 12.5 | 0.397 | 0.396 | 0.394 | 0.392 | 0.39 | 0.388 | 0.385 | 0.382 | 0.379 | 0.376 | 0.373 | 0.37 | 0.366 | 0.363 | 0.359 | 0.355 | 0.351
| 13 | 0.364 | 0.363 | 0.361 | 0.359 | 0.356 | 0.353 | 0.351 | 0.347 | 0.344 | 0.341 | 0.338 | 0.334 | 0.33 | 0.327 | 0.323 | 0.319 | 0.315
| 13.5 | 0.335 | 0.333 | 0.331 | 0.328 | 0.326 | 0.322 | 0.319 | 0.316 | 0.313 | 0.309 | 0.306 | 0.302 | 0.298 | 0.295 | 0.291 | 0.287 | 0.283
| 14 | 0.308 | 0.306 | 0.304 | 0.301 | 0.298 | 0.295 | 0.291 | 0.288 | 0.284 | 0.281 | 0.277 | 0.274 | 0.27 | 0.266 | 0.262 | 0.258 | 0.254
| 14.5 | 0.284 | 0.282 | 0.279 | 0.276 | 0.273 | 0.269 | 0.266 | 0.262 | 0.259 | 0.255 | 0.251 | 0.248 | 0.244 | 0.24 | 0.236 | 0.232 | 0.228
| 15 | 0.262 | 0.259 | 0.256 | 0.253 | 0.25 | 0.246 | 0.243 | 0.239 | 0.236 | 0.232 | 0.228 | 0.224 | 0.22 | 0.216 | 0.213 | 0.208 | 0.204
| 15.5 | 0.242 | 0.239 | 0.236 | 0.233 | 0.229 | 0.226 | 0.222 | 0.218 | 0.215 | 0.211 | 0.207 | 0.204 | 0.199 | 0.195 | 0.192 | 0.188 | 0.184
| 16 | 0.224 | 0.221 | 0.217 | 0.214 | 0.211 | 0.207 | 0.203 | 0.2 | 0.196 | 0.192 | 0.188 | 0.185 | 0.181 | 0.177 | 0.173 | 0.17 | 0.166
| 16.5 | 0.207 | 0.204 | 0.201 | 0.197 | 0.194 | 0.19 | 0.187 | 0.183 | 0.179 | 0.175 | 0.171 | 0.168 | 0.164 | 0.161 | 0.158 | 0.155 | 0.152
| 17 | 0.193 | 0.19 | 0.186 | 0.183 | 0.179 | 0.176 | 0.172 | 0.168 | 0.164 | 0.161 | 0.157 | 0.154 | 0.151 | 0.148 | 0.145 | 0.142 | 0.139
| 17.5 | 0.18 | 0.177 | 0.173 | 0.17 | 0.166 | 0.163 | 0.159 | 0.155 | 0.152 | 0.148 | 0.145 | 0.142 | 0.139 | 0.136 | 0.134 | 0.131 | 0.129
| 18 | 0.169 | 0.166 | 0.162 | 0.158 | 0.155 | 0.151 | 0.147 | 0.144 | 0.141 | 0.138 | 0.135 | 0.132 | 0.129 | 0.127 | 0.124 | 0.122 | 0.12
| 18.5 | 0.159 | 0.156 | 0.152 | 0.148 | 0.145 | 0.141 | 0.138 | 0.135 | 0.132 | 0.129 | 0.126 | 0.123 | 0.121 | 0.119 | 0.116 | 0.114 | 0.112
| 19 | 0.15 | 0.147 | 0.143 | 0.139 | 0.136 | 0.133 | 0.13 | 0.127 | 0.124 | 0.121 | 0.119 | 0.116 | 0.114 | 0.112 | 0.11 | 0.108 | 0.106
| 19.5 | 0.143 | 0.139 | 0.135 | 0.132 | 0.129 | 0.126 | 0.123 | 0.12 | 0.117 | 0.115 | 0.112 | 0.11 | 0.108 | 0.106 | 0.104 | 0.102 | 0.1
| 20 | 0.136 | 0.132 | 0.129 | 0.125 | 0.122 | 0.119 | 0.117 | 0.114 | 0.112 | 0.109 | 0.107 | 0.105 | 0.103 | 0.101 | 0.099 | 0.097 | 0.096
| 20.5 | 0.122 | 0.119 | 0.116 | 0.112 | 0.11 | 0.107 | 0.105 | 0.102 | 0.101 | 0.098 | 0.096 | 0.094 | 0.093 | 0.091 | 0.089 | 0.087 | 0.086
| 21 | 0.11 | 0.107 | 0.104 | 0.101 | 0.099 | 0.096 | 0.095 | 0.092 | 0.091 | 0.088 | 0.087 | 0.085 | 0.083 | 0.082 | 0.08 | 0.079 | 0.078
| 21.5 | 0.099 | 0.096 | 0.094 | 0.091 | 0.089 | 0.087 | 0.085 | 0.083 | 0.082 | 0.079 | 0.078 | 0.077 | 0.075 | 0.074 | 0.072 | 0.071 | 0.07
| 22 | 0.089 | 0.086 | 0.084 | 0.082 | 0.08 | 0.078 | 0.077 | 0.075 | 0.073 | 0.071 | 0.07 | 0.069 | 0.067 | 0.066 | 0.065 | 0.063 | 0.063
| 22.5 | 0.08 | 0.077 | 0.076 | 0.073 | 0.071 | 0.07 | 0.069 | 0.067 | 0.066 | 0.064 | 0.063 | 0.062 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056
| 23 | 0.071 | 0.069 | 0.068 | 0.066 | 0.064 | 0.062 | 0.061 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05
| 23.5 | 0.064 | 0.062 | 0.061 | 0.059 | 0.057 | 0.056 | 0.055 | 0.053 | 0.053 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.045
| 24 | 0.057 | 0.056 | 0.054 | 0.053 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.043 | 0.042 | 0.041 | 0.04
| 24.5 | 0.052 | 0.05 | 0.049 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.041 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037 | 0.036
| 25 | 0.047 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.037 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.033 | 0.033
| 25.5 | 0.043 | 0.042 | 0.041 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032 | 0.032 | 0.031 | 0.031 | 0.03
| 26 | 0.04 | 0.039 | 0.038 | 0.037 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032 | 0.031 | 0.031 | 0.03 | 0.03 | 0.029 | 0.029 | 0.028