## Sheet1
PROPERTIES
General
Name | N163-6.X MW 50-60 Hz vM7_5940
Manufacturer | Nordex
Hub Height | 118 | 138 | 148 | 158.5 | 164
Power
Rated Power | 5940
Peak Power | 5940
Power Regulation Type | Pitch
Voltage | 920
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | -
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -40
Low Temperature Restart | -20
High Temperature Shutdown | 40
High Temperature Restart | 50
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 39.5
Design TI | 0.35

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 5 | 7 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 28 | 30 | 32 | 34 | 37 | 39
| 3.5 | 81 | 85 | 89 | 93 | 97 | 102 | 106 | 110 | 114 | 118 | 122 | 127 | 131 | 135 | 139 | 143 | 147
| 4 | 183 | 190 | 197 | 204 | 211 | 218 | 225 | 232 | 239 | 246 | 253 | 260 | 267 | 274 | 281 | 288 | 295
| 4.5 | 311 | 322 | 332 | 343 | 353 | 364 | 374 | 385 | 396 | 406 | 417 | 427 | 438 | 448 | 459 | 469 | 480
| 5 | 465 | 480 | 495 | 509 | 524 | 539 | 554 | 569 | 583 | 598 | 613 | 628 | 643 | 657 | 672 | 687 | 702
| 5.5 | 647 | 667 | 687 | 706 | 726 | 746 | 766 | 786 | 806 | 826 | 845 | 865 | 885 | 905 | 925 | 944 | 964
| 6 | 862 | 887 | 913 | 939 | 965 | 991 | 1016 | 1042 | 1068 | 1094 | 1119 | 1145 | 1171 | 1197 | 1222 | 1248 | 1274
| 6.5 | 1114 | 1146 | 1179 | 1212 | 1244 | 1277 | 1310 | 1343 | 1375 | 1408 | 1441 | 1473 | 1506 | 1539 | 1571 | 1604 | 1637
| 7 | 1407 | 1448 | 1489 | 1529 | 1570 | 1611 | 1652 | 1692 | 1733 | 1774 | 1815 | 1855 | 1896 | 1937 | 1977 | 2018 | 2059
| 7.5 | 1741 | 1791 | 1841 | 1891 | 1941 | 1991 | 2040 | 2090 | 2140 | 2190 | 2240 | 2290 | 2340 | 2389 | 2439 | 2489 | 2539
| 8 | 2094 | 2154 | 2214 | 2273 | 2333 | 2392 | 2452 | 2512 | 2571 | 2631 | 2690 | 2750 | 2809 | 2868 | 2928 | 2987 | 3046
| 8.5 | 2445 | 2514 | 2583 | 2652 | 2722 | 2791 | 2860 | 2929 | 2998 | 3067 | 3136 | 3205 | 3274 | 3343 | 3412 | 3480 | 3549
| 9 | 2780 | 2859 | 2937 | 3016 | 3094 | 3172 | 3250 | 3329 | 3407 | 3485 | 3563 | 3641 | 3719 | 3797 | 3875 | 3953 | 4031
| 9.5 | 3092 | 3179 | 3265 | 3352 | 3439 | 3526 | 3612 | 3699 | 3786 | 3872 | 3959 | 4045 | 4132 | 4218 | 4304 | 4390 | 4476
| 10 | 3377 | 3471 | 3566 | 3661 | 3755 | 3850 | 3944 | 4038 | 4132 | 4227 | 4321 | 4415 | 4509 | 4603 | 4697 | 4792 | 4884
| 10.5 | 3644 | 3746 | 3847 | 3949 | 4051 | 4153 | 4254 | 4356 | 4457 | 4558 | 4659 | 4761 | 4864 | 4964 | 5057 | 5151 | 5236
| 11 | 3900 | 4008 | 4117 | 4226 | 4334 | 4443 | 4552 | 4660 | 4768 | 4877 | 4987 | 5086 | 5184 | 5276 | 5353 | 5429 | 5497
| 11.5 | 4149 | 4265 | 4380 | 4496 | 4611 | 4726 | 4841 | 4957 | 5070 | 5172 | 5273 | 5357 | 5437 | 5512 | 5573 | 5634 | 5688
| 12 | 4390 | 4512 | 4634 | 4756 | 4878 | 5000 | 5122 | 5227 | 5328 | 5412 | 5495 | 5563 | 5627 | 5687 | 5733 | 5779 | 5818
| 12.5 | 4622 | 4750 | 4878 | 5006 | 5134 | 5251 | 5358 | 5446 | 5530 | 5597 | 5665 | 5717 | 5766 | 5811 | 5842 | 5874 | 5898
| 13 | 4845 | 4980 | 5113 | 5245 | 5356 | 5456 | 5547 | 5618 | 5685 | 5737 | 5790 | 5827 | 5861 | 5891 | 5908 | 5926 | 5936
| 13.5 | 5064 | 5201 | 5328 | 5442 | 5536 | 5619 | 5693 | 5748 | 5800 | 5837 | 5874 | 5897 | 5917 | 5933 | 5936 | 5939 | 5940
| 14 | 5273 | 5395 | 5504 | 5600 | 5677 | 5744 | 5802 | 5842 | 5879 | 5902 | 5924 | 5933 | 5938 | 5940 | 5940 | 5940 | 5940
| 14.5 | 5447 | 5552 | 5644 | 5724 | 5784 | 5836 | 5878 | 5904 | 5926 | 5933 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 15 | 5588 | 5676 | 5751 | 5814 | 5859 | 5895 | 5923 | 5933 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 15.5 | 5700 | 5771 | 5829 | 5877 | 5907 | 5928 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 16 | 5787 | 5842 | 5885 | 5917 | 5932 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 16.5 | 5853 | 5892 | 5920 | 5938 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 17 | 5899 | 5924 | 5938 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 17.5 | 5928 | 5938 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 18 | 5939 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 18.5 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 19 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 19.5 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 20 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 20.5 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 21 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 21.5 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 22 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794 | 5794
| 22.5 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528 | 5528
| 23 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 23.5 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012
| 24 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760
| 24.5 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508
| 25 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264
| 25.5 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019
| 26 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872
| 3.5 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86
| 4 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845
| 4.5 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831
| 5 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82
| 5.5 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813 | 0.813
| 6 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808 | 0.808
| 6.5 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804
| 7 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79
| 7.5 | 0.763 | 0.763 | 0.763 | 0.763 | 0.763 | 0.763 | 0.763 | 0.763 | 0.763 | 0.763 | 0.763 | 0.763 | 0.763 | 0.763 | 0.763 | 0.763 | 0.763
| 8 | 0.728 | 0.728 | 0.728 | 0.728 | 0.728 | 0.728 | 0.728 | 0.728 | 0.728 | 0.728 | 0.728 | 0.728 | 0.728 | 0.728 | 0.728 | 0.728 | 0.728
| 8.5 | 0.687 | 0.687 | 0.687 | 0.687 | 0.687 | 0.687 | 0.687 | 0.687 | 0.687 | 0.687 | 0.687 | 0.687 | 0.687 | 0.687 | 0.687 | 0.687 | 0.687
| 9 | 0.644 | 0.644 | 0.644 | 0.644 | 0.644 | 0.644 | 0.644 | 0.644 | 0.644 | 0.644 | 0.644 | 0.644 | 0.644 | 0.644 | 0.644 | 0.644 | 0.644
| 9.5 | 0.599 | 0.599 | 0.599 | 0.599 | 0.599 | 0.599 | 0.599 | 0.599 | 0.599 | 0.599 | 0.599 | 0.599 | 0.599 | 0.599 | 0.598 | 0.598 | 0.597
| 10 | 0.553 | 0.553 | 0.553 | 0.553 | 0.553 | 0.553 | 0.553 | 0.553 | 0.553 | 0.553 | 0.553 | 0.553 | 0.553 | 0.552 | 0.55 | 0.549 | 0.548
| 10.5 | 0.509 | 0.509 | 0.509 | 0.509 | 0.509 | 0.509 | 0.509 | 0.509 | 0.509 | 0.508 | 0.507 | 0.506 | 0.505 | 0.503 | 0.501 | 0.499 | 0.497
| 11 | 0.465 | 0.465 | 0.465 | 0.465 | 0.465 | 0.465 | 0.465 | 0.464 | 0.464 | 0.462 | 0.461 | 0.459 | 0.457 | 0.455 | 0.453 | 0.45 | 0.448
| 11.5 | 0.425 | 0.425 | 0.425 | 0.425 | 0.425 | 0.425 | 0.424 | 0.422 | 0.421 | 0.419 | 0.417 | 0.415 | 0.413 | 0.41 | 0.408 | 0.405 | 0.402
| 12 | 0.39 | 0.39 | 0.39 | 0.39 | 0.389 | 0.387 | 0.386 | 0.384 | 0.382 | 0.38 | 0.378 | 0.375 | 0.373 | 0.37 | 0.367 | 0.364 | 0.361
| 12.5 | 0.359 | 0.358 | 0.358 | 0.357 | 0.355 | 0.354 | 0.352 | 0.35 | 0.348 | 0.345 | 0.343 | 0.34 | 0.337 | 0.334 | 0.331 | 0.328 | 0.325
| 13 | 0.331 | 0.33 | 0.329 | 0.327 | 0.326 | 0.324 | 0.321 | 0.319 | 0.317 | 0.314 | 0.311 | 0.308 | 0.305 | 0.302 | 0.299 | 0.295 | 0.292
| 13.5 | 0.305 | 0.304 | 0.302 | 0.3 | 0.298 | 0.296 | 0.294 | 0.291 | 0.288 | 0.285 | 0.283 | 0.279 | 0.276 | 0.273 | 0.27 | 0.266 | 0.263
| 14 | 0.281 | 0.28 | 0.278 | 0.276 | 0.274 | 0.271 | 0.269 | 0.266 | 0.263 | 0.26 | 0.257 | 0.254 | 0.25 | 0.247 | 0.244 | 0.24 | 0.237
| 14.5 | 0.26 | 0.258 | 0.256 | 0.254 | 0.251 | 0.249 | 0.246 | 0.243 | 0.24 | 0.237 | 0.234 | 0.231 | 0.227 | 0.224 | 0.221 | 0.217 | 0.214
| 15 | 0.24 | 0.238 | 0.236 | 0.234 | 0.231 | 0.229 | 0.226 | 0.223 | 0.22 | 0.216 | 0.213 | 0.21 | 0.207 | 0.203 | 0.2 | 0.196 | 0.193
| 15.5 | 0.223 | 0.22 | 0.218 | 0.216 | 0.213 | 0.21 | 0.207 | 0.204 | 0.201 | 0.198 | 0.194 | 0.191 | 0.188 | 0.184 | 0.181 | 0.177 | 0.174
| 16 | 0.206 | 0.204 | 0.201 | 0.199 | 0.196 | 0.193 | 0.19 | 0.187 | 0.184 | 0.181 | 0.177 | 0.174 | 0.171 | 0.167 | 0.164 | 0.161 | 0.158
| 16.5 | 0.192 | 0.189 | 0.187 | 0.184 | 0.181 | 0.178 | 0.175 | 0.172 | 0.169 | 0.166 | 0.162 | 0.159 | 0.156 | 0.152 | 0.149 | 0.146 | 0.144
| 17 | 0.179 | 0.176 | 0.174 | 0.171 | 0.168 | 0.165 | 0.162 | 0.159 | 0.156 | 0.152 | 0.149 | 0.146 | 0.143 | 0.14 | 0.137 | 0.134 | 0.132
| 17.5 | 0.168 | 0.165 | 0.162 | 0.159 | 0.156 | 0.153 | 0.15 | 0.147 | 0.144 | 0.141 | 0.137 | 0.135 | 0.132 | 0.129 | 0.127 | 0.124 | 0.122
| 18 | 0.158 | 0.155 | 0.152 | 0.149 | 0.146 | 0.143 | 0.14 | 0.137 | 0.134 | 0.131 | 0.128 | 0.125 | 0.123 | 0.12 | 0.118 | 0.116 | 0.114
| 18.5 | 0.149 | 0.146 | 0.143 | 0.14 | 0.137 | 0.134 | 0.131 | 0.128 | 0.125 | 0.122 | 0.12 | 0.117 | 0.115 | 0.113 | 0.11 | 0.108 | 0.106
| 19 | 0.141 | 0.138 | 0.135 | 0.132 | 0.129 | 0.126 | 0.123 | 0.12 | 0.118 | 0.115 | 0.113 | 0.11 | 0.108 | 0.106 | 0.104 | 0.102 | 0.1
| 19.5 | 0.135 | 0.131 | 0.128 | 0.125 | 0.122 | 0.119 | 0.116 | 0.114 | 0.111 | 0.109 | 0.107 | 0.105 | 0.103 | 0.101 | 0.099 | 0.097 | 0.095
| 20 | 0.129 | 0.125 | 0.122 | 0.119 | 0.116 | 0.114 | 0.111 | 0.108 | 0.106 | 0.104 | 0.102 | 0.1 | 0.098 | 0.096 | 0.094 | 0.092 | 0.091
| 20.5 | 0.116 | 0.112 | 0.11 | 0.107 | 0.104 | 0.102 | 0.1 | 0.097 | 0.095 | 0.093 | 0.092 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083 | 0.082
| 21 | 0.104 | 0.101 | 0.099 | 0.096 | 0.094 | 0.092 | 0.09 | 0.087 | 0.086 | 0.084 | 0.083 | 0.081 | 0.079 | 0.078 | 0.076 | 0.075 | 0.074
| 21.5 | 0.094 | 0.091 | 0.089 | 0.087 | 0.085 | 0.083 | 0.081 | 0.079 | 0.077 | 0.076 | 0.074 | 0.073 | 0.071 | 0.07 | 0.069 | 0.067 | 0.066
| 22 | 0.084 | 0.082 | 0.08 | 0.078 | 0.076 | 0.075 | 0.073 | 0.071 | 0.069 | 0.068 | 0.067 | 0.065 | 0.064 | 0.063 | 0.061 | 0.06 | 0.06
| 22.5 | 0.076 | 0.073 | 0.071 | 0.07 | 0.068 | 0.067 | 0.065 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053
| 23 | 0.068 | 0.066 | 0.064 | 0.062 | 0.061 | 0.06 | 0.058 | 0.057 | 0.056 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.048
| 23.5 | 0.061 | 0.059 | 0.057 | 0.056 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.043
| 24 | 0.054 | 0.053 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.045 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038
| 24.5 | 0.049 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034
| 25 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032 | 0.032 | 0.031
| 25.5 | 0.041 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.032 | 0.031 | 0.03 | 0.03 | 0.029 | 0.029
| 26 | 0.038 | 0.037 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032 | 0.031 | 0.031 | 0.03 | 0.029 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027