## Sheet1
PROPERTIES
General
Name | N163-6.X MW 50-60 Hz vM9_5270
Manufacturer | Nordex
Hub Height | 118 | 138 | 148 | 158.5 | 164
Power
Rated Power | 5270
Peak Power | 5270
Power Regulation Type | Pitch
Voltage | 920
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | -
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -40
Low Temperature Restart | -20
High Temperature Shutdown | 40
High Temperature Restart | 50
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 39.5
Design TI | 0.35

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 22 | 24 | 26 | 28 | 30 | 32 | 34 | 37 | 39
| 3.5 | 114 | 118 | 122 | 127 | 131 | 135 | 139 | 143 | 147
| 4 | 239 | 246 | 253 | 260 | 267 | 274 | 281 | 288 | 295
| 4.5 | 396 | 406 | 417 | 427 | 438 | 448 | 459 | 469 | 480
| 5 | 583 | 598 | 613 | 628 | 643 | 657 | 672 | 687 | 702
| 5.5 | 806 | 826 | 845 | 865 | 885 | 905 | 925 | 944 | 964
| 6 | 1068 | 1094 | 1119 | 1145 | 1171 | 1197 | 1222 | 1248 | 1274
| 6.5 | 1375 | 1407 | 1440 | 1473 | 1505 | 1538 | 1570 | 1603 | 1636
| 7 | 1713 | 1753 | 1793 | 1834 | 1874 | 1914 | 1954 | 1995 | 2035
| 7.5 | 2053 | 2100 | 2148 | 2196 | 2244 | 2292 | 2340 | 2387 | 2435
| 8 | 2378 | 2433 | 2488 | 2543 | 2598 | 2654 | 2709 | 2764 | 2819
| 8.5 | 2677 | 2738 | 2800 | 2862 | 2924 | 2986 | 3047 | 3109 | 3171
| 9 | 2947 | 3015 | 3083 | 3151 | 3219 | 3287 | 3354 | 3422 | 3490
| 9.5 | 3201 | 3275 | 3348 | 3422 | 3495 | 3569 | 3642 | 3715 | 3789
| 10 | 3446 | 3525 | 3604 | 3682 | 3761 | 3840 | 3919 | 3998 | 4076
| 10.5 | 3682 | 3767 | 3851 | 3935 | 4019 | 4103 | 4187 | 4271 | 4356
| 11 | 3909 | 3998 | 4087 | 4176 | 4265 | 4354 | 4444 | 4534 | 4614
| 11.5 | 4126 | 4220 | 4314 | 4408 | 4503 | 4596 | 4679 | 4762 | 4827
| 12 | 4338 | 4436 | 4535 | 4633 | 4718 | 4802 | 4870 | 4938 | 4991
| 12.5 | 4545 | 4648 | 4736 | 4822 | 4893 | 4962 | 5017 | 5072 | 5112
| 13 | 4735 | 4824 | 4898 | 4970 | 5027 | 5083 | 5126 | 5168 | 5196
| 13.5 | 4888 | 4963 | 5023 | 5081 | 5126 | 5169 | 5199 | 5229 | 5245
| 14 | 5009 | 5070 | 5118 | 5163 | 5195 | 5226 | 5244 | 5262 | 5266
| 14.5 | 5104 | 5153 | 5188 | 5221 | 5241 | 5259 | 5265 | 5270 | 5270
| 15 | 5176 | 5212 | 5235 | 5256 | 5264 | 5270 | 5270 | 5270 | 5270
| 15.5 | 5227 | 5251 | 5261 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 16 | 5257 | 5269 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 16.5 | 5269 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 17 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 17.5 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 18 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 18.5 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 19 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 19.5 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 20 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 20.5 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 21 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 21.5 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 22 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 22.5 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 23 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 23.5 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012
| 24 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760
| 24.5 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508 | 4508
| 25 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264 | 4264
| 25.5 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019 | 4019
| 26 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774 | 3774

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872
| 3.5 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86
| 4 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845 | 0.845
| 4.5 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831 | 0.831
| 5 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82
| 5.5 | 0.814 | 0.814 | 0.814 | 0.814 | 0.814 | 0.814 | 0.814 | 0.814 | 0.814
| 6 | 0.803 | 0.803 | 0.803 | 0.803 | 0.803 | 0.803 | 0.803 | 0.803 | 0.803
| 6.5 | 0.776 | 0.776 | 0.776 | 0.776 | 0.776 | 0.776 | 0.776 | 0.776 | 0.776
| 7 | 0.737 | 0.737 | 0.737 | 0.737 | 0.737 | 0.737 | 0.737 | 0.737 | 0.737
| 7.5 | 0.692 | 0.692 | 0.692 | 0.692 | 0.692 | 0.692 | 0.692 | 0.692 | 0.692
| 8 | 0.643 | 0.643 | 0.643 | 0.643 | 0.643 | 0.643 | 0.643 | 0.643 | 0.643
| 8.5 | 0.592 | 0.592 | 0.592 | 0.592 | 0.592 | 0.592 | 0.592 | 0.592 | 0.592
| 9 | 0.541 | 0.541 | 0.541 | 0.541 | 0.541 | 0.541 | 0.541 | 0.541 | 0.541
| 9.5 | 0.491 | 0.491 | 0.491 | 0.491 | 0.491 | 0.491 | 0.491 | 0.491 | 0.491
| 10 | 0.444 | 0.444 | 0.444 | 0.444 | 0.444 | 0.444 | 0.444 | 0.444 | 0.444
| 10.5 | 0.402 | 0.402 | 0.402 | 0.402 | 0.402 | 0.402 | 0.401 | 0.401 | 0.4
| 11 | 0.365 | 0.365 | 0.365 | 0.365 | 0.365 | 0.364 | 0.363 | 0.362 | 0.361
| 11.5 | 0.334 | 0.334 | 0.333 | 0.332 | 0.331 | 0.33 | 0.329 | 0.328 | 0.326
| 12 | 0.305 | 0.305 | 0.304 | 0.303 | 0.301 | 0.3 | 0.299 | 0.297 | 0.295
| 12.5 | 0.279 | 0.278 | 0.277 | 0.276 | 0.275 | 0.273 | 0.271 | 0.269 | 0.267
| 13 | 0.256 | 0.255 | 0.254 | 0.252 | 0.25 | 0.249 | 0.247 | 0.245 | 0.243
| 13.5 | 0.235 | 0.234 | 0.232 | 0.231 | 0.229 | 0.227 | 0.225 | 0.223 | 0.221
| 14 | 0.216 | 0.215 | 0.213 | 0.211 | 0.209 | 0.207 | 0.205 | 0.203 | 0.201
| 14.5 | 0.199 | 0.197 | 0.195 | 0.194 | 0.192 | 0.19 | 0.187 | 0.185 | 0.183
| 15 | 0.183 | 0.182 | 0.18 | 0.178 | 0.175 | 0.173 | 0.171 | 0.169 | 0.166
| 15.5 | 0.169 | 0.167 | 0.165 | 0.163 | 0.161 | 0.159 | 0.156 | 0.154 | 0.152
| 16 | 0.156 | 0.154 | 0.152 | 0.15 | 0.148 | 0.145 | 0.143 | 0.141 | 0.138
| 16.5 | 0.144 | 0.142 | 0.14 | 0.138 | 0.136 | 0.134 | 0.131 | 0.129 | 0.127
| 17 | 0.134 | 0.132 | 0.13 | 0.128 | 0.125 | 0.123 | 0.121 | 0.119 | 0.116
| 17.5 | 0.125 | 0.123 | 0.121 | 0.119 | 0.116 | 0.114 | 0.112 | 0.11 | 0.108
| 18 | 0.117 | 0.115 | 0.113 | 0.111 | 0.108 | 0.106 | 0.104 | 0.102 | 0.1
| 18.5 | 0.11 | 0.108 | 0.106 | 0.104 | 0.101 | 0.099 | 0.098 | 0.096 | 0.094
| 19 | 0.104 | 0.102 | 0.1 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.089
| 19.5 | 0.099 | 0.097 | 0.094 | 0.093 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084
| 20 | 0.094 | 0.092 | 0.09 | 0.088 | 0.087 | 0.085 | 0.083 | 0.082 | 0.08
| 20.5 | 0.085 | 0.083 | 0.081 | 0.079 | 0.078 | 0.076 | 0.075 | 0.074 | 0.072
| 21 | 0.076 | 0.075 | 0.073 | 0.071 | 0.07 | 0.069 | 0.067 | 0.066 | 0.065
| 21.5 | 0.069 | 0.067 | 0.066 | 0.064 | 0.063 | 0.062 | 0.061 | 0.06 | 0.058
| 22 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056 | 0.054 | 0.054 | 0.052
| 22.5 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047
| 23 | 0.049 | 0.048 | 0.047 | 0.046 | 0.046 | 0.045 | 0.043 | 0.043 | 0.042
| 23.5 | 0.044 | 0.043 | 0.042 | 0.041 | 0.041 | 0.04 | 0.039 | 0.038 | 0.038
| 24 | 0.04 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034
| 24.5 | 0.036 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.031 | 0.031 | 0.03
| 25 | 0.032 | 0.032 | 0.031 | 0.03 | 0.03 | 0.029 | 0.029 | 0.028 | 0.028
| 25.5 | 0.03 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.026 | 0.025
| 26 | 0.028 | 0.027 | 0.026 | 0.026 | 0.026 | 0.025 | 0.024 | 0.024 | 0.024