## Sheet1
PROPERTIES
General
Name | N175-6.X MW 50-60 Hz vM10_4250
Manufacturer | Nordex
Hub Height | 142 | 179
Power
Rated Power | 4250
Peak Power | 4250
Power Regulation Type | Pitch
Voltage | 950
Rotor
Rotor diameter | 175
Number of blades | 3
Rated RPM | -
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 20
Restart Wind Speed | 19.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -40
Low Temperature Restart | -20
High Temperature Shutdown | 40
High Temperature Restart | 45
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 39.6
Design TI | 0.35

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 49 | 52 | 54 | 57 | 60 | 63 | 65 | 68 | 71 | 73 | 76 | 79 | 82
| 3.5 | 148 | 154 | 159 | 164 | 169 | 174 | 180 | 185 | 190 | 195 | 201 | 206 | 211
| 4 | 283 | 292 | 300 | 309 | 317 | 326 | 335 | 343 | 352 | 360 | 369 | 378 | 386
| 4.5 | 452 | 465 | 477 | 490 | 503 | 516 | 529 | 541 | 554 | 567 | 580 | 593 | 605
| 5 | 655 | 673 | 690 | 708 | 726 | 744 | 762 | 780 | 797 | 815 | 833 | 851 | 869
| 5.5 | 896 | 920 | 943 | 967 | 991 | 1015 | 1039 | 1062 | 1086 | 1110 | 1134 | 1158 | 1181
| 6 | 1179 | 1210 | 1241 | 1272 | 1303 | 1333 | 1364 | 1395 | 1426 | 1457 | 1487 | 1518 | 1549
| 6.5 | 1488 | 1526 | 1565 | 1603 | 1642 | 1680 | 1719 | 1757 | 1795 | 1834 | 1872 | 1911 | 1949
| 7 | 1796 | 1842 | 1888 | 1934 | 1980 | 2026 | 2072 | 2118 | 2164 | 2210 | 2256 | 2302 | 2348
| 7.5 | 2086 | 2140 | 2193 | 2246 | 2299 | 2352 | 2406 | 2459 | 2512 | 2565 | 2618 | 2671 | 2724
| 8 | 2354 | 2414 | 2473 | 2533 | 2593 | 2653 | 2712 | 2772 | 2832 | 2891 | 2951 | 3011 | 3070
| 8.5 | 2605 | 2671 | 2737 | 2803 | 2869 | 2935 | 3000 | 3066 | 3132 | 3198 | 3263 | 3329 | 3395
| 9 | 2849 | 2920 | 2992 | 3064 | 3136 | 3208 | 3280 | 3351 | 3423 | 3495 | 3565 | 3636 | 3691
| 9.5 | 3074 | 3152 | 3229 | 3307 | 3384 | 3462 | 3539 | 3614 | 3689 | 3755 | 3813 | 3872 | 3914
| 10 | 3288 | 3371 | 3454 | 3537 | 3619 | 3698 | 3776 | 3838 | 3898 | 3950 | 3996 | 4042 | 4072
| 10.5 | 3495 | 3584 | 3670 | 3751 | 3828 | 3893 | 3955 | 4005 | 4053 | 4092 | 4125 | 4158 | 4177
| 11 | 3695 | 3779 | 3858 | 3923 | 3986 | 4037 | 4086 | 4123 | 4157 | 4184 | 4205 | 4227 | 4233
| 11.5 | 3865 | 3933 | 3997 | 4049 | 4098 | 4137 | 4172 | 4197 | 4219 | 4234 | 4242 | 4250 | 4250
| 12 | 3994 | 4049 | 4099 | 4138 | 4174 | 4200 | 4223 | 4235 | 4245 | 4249 | 4249 | 4250 | 4250
| 12.5 | 4094 | 4136 | 4173 | 4199 | 4223 | 4237 | 4248 | 4249 | 4250 | 4249 | 4250 | 4250 | 4250
| 13 | 4168 | 4197 | 4221 | 4236 | 4247 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250
| 13.5 | 4217 | 4234 | 4246 | 4249 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250
| 14 | 4244 | 4248 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250
| 14.5 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250
| 15 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250
| 15.5 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250
| 16 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250
| 16.5 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250
| 17 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250
| 17.5 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250
| 18 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250
| 18.5 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250
| 19 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250
| 19.5 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250
| 20 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250 | 4250

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
TI (%) | 10 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874
| 3.5 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867
| 4 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852
| 4.5 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839
| 5 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83
| 5.5 | 0.819 | 0.819 | 0.819 | 0.819 | 0.819 | 0.819 | 0.819 | 0.819 | 0.819 | 0.819 | 0.819 | 0.819 | 0.819
| 6 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786
| 6.5 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74
| 7 | 0.688 | 0.688 | 0.688 | 0.688 | 0.688 | 0.688 | 0.688 | 0.688 | 0.688 | 0.688 | 0.688 | 0.688 | 0.688
| 7.5 | 0.634 | 0.634 | 0.634 | 0.634 | 0.634 | 0.634 | 0.634 | 0.634 | 0.634 | 0.634 | 0.634 | 0.634 | 0.634
| 8 | 0.579 | 0.579 | 0.579 | 0.579 | 0.579 | 0.579 | 0.579 | 0.579 | 0.579 | 0.579 | 0.579 | 0.579 | 0.578
| 8.5 | 0.523 | 0.523 | 0.523 | 0.523 | 0.523 | 0.523 | 0.523 | 0.523 | 0.523 | 0.523 | 0.522 | 0.521 | 0.52
| 9 | 0.469 | 0.469 | 0.469 | 0.469 | 0.469 | 0.469 | 0.469 | 0.468 | 0.467 | 0.466 | 0.464 | 0.463 | 0.461
| 9.5 | 0.421 | 0.421 | 0.421 | 0.421 | 0.42 | 0.42 | 0.419 | 0.417 | 0.416 | 0.414 | 0.412 | 0.41 | 0.408
| 10 | 0.38 | 0.38 | 0.379 | 0.379 | 0.377 | 0.376 | 0.375 | 0.373 | 0.371 | 0.369 | 0.366 | 0.364 | 0.361
| 10.5 | 0.344 | 0.343 | 0.342 | 0.341 | 0.339 | 0.337 | 0.335 | 0.333 | 0.331 | 0.329 | 0.326 | 0.324 | 0.32
| 11 | 0.311 | 0.31 | 0.309 | 0.307 | 0.305 | 0.303 | 0.301 | 0.298 | 0.296 | 0.293 | 0.29 | 0.288 | 0.284
| 11.5 | 0.282 | 0.281 | 0.279 | 0.277 | 0.275 | 0.272 | 0.27 | 0.267 | 0.265 | 0.262 | 0.259 | 0.256 | 0.253
| 12 | 0.256 | 0.254 | 0.252 | 0.25 | 0.248 | 0.245 | 0.243 | 0.24 | 0.237 | 0.234 | 0.231 | 0.228 | 0.225
| 12.5 | 0.233 | 0.231 | 0.228 | 0.226 | 0.223 | 0.221 | 0.218 | 0.215 | 0.213 | 0.21 | 0.207 | 0.204 | 0.2
| 13 | 0.212 | 0.209 | 0.207 | 0.204 | 0.202 | 0.199 | 0.196 | 0.194 | 0.191 | 0.188 | 0.185 | 0.182 | 0.178
| 13.5 | 0.192 | 0.19 | 0.188 | 0.185 | 0.182 | 0.18 | 0.177 | 0.174 | 0.171 | 0.168 | 0.165 | 0.162 | 0.159
| 14 | 0.175 | 0.173 | 0.17 | 0.167 | 0.165 | 0.162 | 0.159 | 0.156 | 0.153 | 0.15 | 0.147 | 0.145 | 0.142
| 14.5 | 0.16 | 0.157 | 0.155 | 0.152 | 0.149 | 0.146 | 0.144 | 0.141 | 0.138 | 0.135 | 0.132 | 0.13 | 0.127
| 15 | 0.146 | 0.143 | 0.141 | 0.138 | 0.135 | 0.132 | 0.13 | 0.127 | 0.124 | 0.122 | 0.12 | 0.117 | 0.115
| 15.5 | 0.133 | 0.131 | 0.128 | 0.125 | 0.123 | 0.12 | 0.117 | 0.115 | 0.113 | 0.111 | 0.108 | 0.106 | 0.104
| 16 | 0.122 | 0.119 | 0.117 | 0.114 | 0.112 | 0.109 | 0.107 | 0.105 | 0.103 | 0.101 | 0.099 | 0.097 | 0.095
| 16.5 | 0.112 | 0.109 | 0.107 | 0.104 | 0.102 | 0.1 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.089 | 0.087
| 17 | 0.103 | 0.1 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.087 | 0.085 | 0.083 | 0.082 | 0.08
| 17.5 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.085 | 0.084 | 0.082 | 0.08 | 0.079 | 0.077 | 0.076 | 0.075
| 18 | 0.089 | 0.087 | 0.085 | 0.083 | 0.081 | 0.08 | 0.078 | 0.076 | 0.075 | 0.074 | 0.072 | 0.071 | 0.07
| 18.5 | 0.083 | 0.081 | 0.08 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.071 | 0.069 | 0.068 | 0.067 | 0.066
| 19 | 0.077 | 0.075 | 0.074 | 0.072 | 0.07 | 0.069 | 0.067 | 0.066 | 0.065 | 0.064 | 0.063 | 0.062 | 0.061
| 19.5 | 0.07 | 0.068 | 0.067 | 0.065 | 0.064 | 0.063 | 0.061 | 0.06 | 0.06 | 0.058 | 0.057 | 0.056 | 0.055
| 20 | 0.063 | 0.061 | 0.06 | 0.059 | 0.057 | 0.057 | 0.055 | 0.054 | 0.054 | 0.052 | 0.051 | 0.051 | 0.05