## Sheet1
PROPERTIES
General
Name | N175-6.X MW 50-60 Hz vM12_3700
Manufacturer | Nordex
Hub Height | 142 | 179
Power
Rated Power | 3700
Peak Power | 3700
Power Regulation Type | Pitch
Voltage | 950
Rotor
Rotor diameter | 175
Number of blades | 3
Rated RPM | -
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 20
Restart Wind Speed | 19.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -40
Low Temperature Restart | -20
High Temperature Shutdown | 40
High Temperature Restart | 45
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 39.6
Design TI | 0.35

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 49 | 52 | 54 | 57 | 60 | 63 | 65 | 68 | 71 | 74 | 76 | 79 | 82
| 3.5 | 148 | 154 | 159 | 164 | 169 | 174 | 180 | 185 | 190 | 195 | 201 | 206 | 211
| 4 | 283 | 292 | 300 | 309 | 317 | 326 | 335 | 343 | 352 | 360 | 369 | 378 | 386
| 4.5 | 452 | 465 | 477 | 490 | 503 | 516 | 529 | 541 | 554 | 567 | 580 | 593 | 605
| 5 | 655 | 673 | 690 | 708 | 726 | 744 | 762 | 780 | 797 | 815 | 833 | 851 | 869
| 5.5 | 896 | 919 | 943 | 967 | 991 | 1015 | 1039 | 1062 | 1086 | 1110 | 1134 | 1157 | 1181
| 6 | 1171 | 1202 | 1232 | 1263 | 1294 | 1324 | 1355 | 1385 | 1416 | 1447 | 1477 | 1508 | 1538
| 6.5 | 1454 | 1492 | 1530 | 1567 | 1605 | 1643 | 1680 | 1718 | 1756 | 1793 | 1831 | 1868 | 1906
| 7 | 1727 | 1772 | 1816 | 1861 | 1905 | 1949 | 1994 | 2038 | 2082 | 2127 | 2171 | 2215 | 2259
| 7.5 | 1978 | 2029 | 2079 | 2130 | 2180 | 2231 | 2281 | 2332 | 2382 | 2433 | 2483 | 2534 | 2584
| 8 | 2212 | 2268 | 2324 | 2380 | 2437 | 2493 | 2549 | 2605 | 2662 | 2718 | 2774 | 2830 | 2886
| 8.5 | 2437 | 2499 | 2560 | 2622 | 2684 | 2746 | 2808 | 2869 | 2931 | 2992 | 3054 | 3116 | 3169
| 9 | 2647 | 2714 | 2781 | 2847 | 2914 | 2981 | 3048 | 3114 | 3180 | 3240 | 3291 | 3343 | 3385
| 9.5 | 2843 | 2915 | 2987 | 3059 | 3130 | 3200 | 3269 | 3324 | 3379 | 3426 | 3466 | 3506 | 3536
| 10 | 3033 | 3110 | 3185 | 3257 | 3325 | 3382 | 3438 | 3480 | 3523 | 3558 | 3587 | 3615 | 3635
| 10.5 | 3215 | 3290 | 3357 | 3415 | 3470 | 3514 | 3558 | 3589 | 3620 | 3644 | 3662 | 3679 | 3688
| 11 | 3368 | 3429 | 3483 | 3529 | 3571 | 3604 | 3636 | 3655 | 3675 | 3688 | 3694 | 3700 | 3700
| 11.5 | 3484 | 3533 | 3575 | 3608 | 3639 | 3660 | 3680 | 3689 | 3697 | 3700 | 3700 | 3700 | 3700
| 12 | 3573 | 3609 | 3639 | 3662 | 3681 | 3690 | 3699 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 12.5 | 3637 | 3662 | 3680 | 3691 | 3699 | 3699 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 13 | 3677 | 3691 | 3699 | 3700 | 3700 | 3699 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 13.5 | 3697 | 3700 | 3700 | 3700 | 3700 | 3699 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 14 | 3700 | 3700 | 3700 | 3700 | 3700 | 3699 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 14.5 | 3700 | 3700 | 3700 | 3700 | 3700 | 3699 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 15 | 3700 | 3700 | 3700 | 3700 | 3700 | 3699 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 15.5 | 3700 | 3700 | 3700 | 3700 | 3700 | 3699 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 16 | 3700 | 3700 | 3700 | 3700 | 3700 | 3699 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 16.5 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 17 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 17.5 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 18 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 18.5 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 19 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 19.5 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 20 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
TI (%) | 10 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874
| 3.5 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867
| 4 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852
| 4.5 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839
| 5 | 0.829 | 0.829 | 0.829 | 0.829 | 0.829 | 0.829 | 0.829 | 0.829 | 0.829 | 0.829 | 0.829 | 0.829 | 0.829
| 5.5 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804
| 6 | 0.761 | 0.761 | 0.761 | 0.761 | 0.761 | 0.761 | 0.761 | 0.761 | 0.761 | 0.761 | 0.761 | 0.761 | 0.761
| 6.5 | 0.708 | 0.708 | 0.708 | 0.708 | 0.708 | 0.708 | 0.708 | 0.708 | 0.708 | 0.708 | 0.708 | 0.708 | 0.708
| 7 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651
| 7.5 | 0.593 | 0.593 | 0.593 | 0.593 | 0.593 | 0.593 | 0.593 | 0.593 | 0.593 | 0.593 | 0.594 | 0.594 | 0.593
| 8 | 0.535 | 0.535 | 0.535 | 0.535 | 0.535 | 0.535 | 0.535 | 0.535 | 0.536 | 0.535 | 0.535 | 0.534 | 0.533
| 8.5 | 0.479 | 0.479 | 0.479 | 0.479 | 0.479 | 0.479 | 0.479 | 0.478 | 0.478 | 0.477 | 0.475 | 0.474 | 0.472
| 9 | 0.428 | 0.428 | 0.428 | 0.428 | 0.428 | 0.427 | 0.426 | 0.425 | 0.423 | 0.422 | 0.42 | 0.418 | 0.415
| 9.5 | 0.384 | 0.384 | 0.384 | 0.383 | 0.382 | 0.38 | 0.379 | 0.377 | 0.375 | 0.373 | 0.371 | 0.369 | 0.366
| 10 | 0.346 | 0.345 | 0.344 | 0.343 | 0.341 | 0.339 | 0.338 | 0.335 | 0.333 | 0.331 | 0.328 | 0.326 | 0.323
| 10.5 | 0.312 | 0.31 | 0.309 | 0.307 | 0.305 | 0.303 | 0.301 | 0.299 | 0.296 | 0.294 | 0.291 | 0.288 | 0.285
| 11 | 0.281 | 0.28 | 0.278 | 0.276 | 0.274 | 0.271 | 0.269 | 0.266 | 0.264 | 0.261 | 0.258 | 0.255 | 0.252
| 11.5 | 0.254 | 0.252 | 0.25 | 0.248 | 0.246 | 0.243 | 0.241 | 0.238 | 0.235 | 0.232 | 0.229 | 0.226 | 0.223
| 12 | 0.23 | 0.228 | 0.225 | 0.223 | 0.221 | 0.218 | 0.215 | 0.212 | 0.21 | 0.207 | 0.204 | 0.201 | 0.197
| 12.5 | 0.208 | 0.206 | 0.203 | 0.201 | 0.198 | 0.195 | 0.193 | 0.19 | 0.187 | 0.184 | 0.181 | 0.178 | 0.175
| 13 | 0.188 | 0.186 | 0.183 | 0.181 | 0.178 | 0.175 | 0.173 | 0.17 | 0.167 | 0.164 | 0.161 | 0.158 | 0.155
| 13.5 | 0.171 | 0.168 | 0.166 | 0.163 | 0.16 | 0.158 | 0.155 | 0.152 | 0.149 | 0.146 | 0.143 | 0.14 | 0.138
| 14 | 0.155 | 0.153 | 0.15 | 0.147 | 0.145 | 0.142 | 0.139 | 0.136 | 0.133 | 0.131 | 0.128 | 0.126 | 0.123
| 14.5 | 0.141 | 0.138 | 0.136 | 0.133 | 0.13 | 0.128 | 0.125 | 0.122 | 0.12 | 0.117 | 0.115 | 0.113 | 0.111
| 15 | 0.128 | 0.126 | 0.123 | 0.12 | 0.118 | 0.115 | 0.113 | 0.111 | 0.108 | 0.106 | 0.104 | 0.102 | 0.1
| 15.5 | 0.117 | 0.114 | 0.112 | 0.109 | 0.107 | 0.105 | 0.102 | 0.1 | 0.098 | 0.096 | 0.095 | 0.093 | 0.091
| 16 | 0.107 | 0.104 | 0.102 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083
| 16.5 | 0.098 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.085 | 0.084 | 0.082 | 0.081 | 0.079 | 0.078 | 0.076
| 17 | 0.09 | 0.088 | 0.086 | 0.084 | 0.082 | 0.08 | 0.079 | 0.077 | 0.076 | 0.074 | 0.073 | 0.072 | 0.071
| 17.5 | 0.083 | 0.081 | 0.08 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.07 | 0.069 | 0.068 | 0.067 | 0.066
| 18 | 0.078 | 0.076 | 0.074 | 0.073 | 0.071 | 0.07 | 0.068 | 0.067 | 0.066 | 0.065 | 0.064 | 0.062 | 0.061
| 18.5 | 0.073 | 0.071 | 0.07 | 0.068 | 0.067 | 0.066 | 0.064 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058
| 19 | 0.067 | 0.065 | 0.065 | 0.063 | 0.062 | 0.061 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053
| 19.5 | 0.061 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.05 | 0.049
| 20 | 0.055 | 0.054 | 0.053 | 0.051 | 0.051 | 0.05 | 0.048 | 0.048 | 0.047 | 0.046 | 0.045 | 0.045 | 0.044