## Sheet1
PROPERTIES
General
Name | N175-6.X MW 50-60 Hz vM13_3430
Manufacturer | Nordex
Hub Height | 142 | 179
Power
Rated Power | 3430
Peak Power | 3430
Power Regulation Type | Pitch
Voltage | 950
Rotor
Rotor diameter | 175
Number of blades | 3
Rated RPM | -
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 20
Restart Wind Speed | 19.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -40
Low Temperature Restart | -20
High Temperature Shutdown | 40
High Temperature Restart | 45
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 39.6
Design TI | 0.35

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 49 | 52 | 54 | 57 | 60 | 63 | 65 | 68 | 71 | 74 | 76 | 79 | 82
| 3.5 | 148 | 154 | 159 | 164 | 169 | 174 | 180 | 185 | 190 | 195 | 201 | 206 | 211
| 4 | 283 | 292 | 300 | 309 | 317 | 326 | 335 | 343 | 352 | 360 | 369 | 378 | 386
| 4.5 | 452 | 465 | 477 | 490 | 503 | 516 | 529 | 541 | 554 | 567 | 580 | 593 | 605
| 5 | 655 | 673 | 690 | 708 | 726 | 744 | 762 | 780 | 797 | 815 | 833 | 851 | 869
| 5.5 | 895 | 919 | 943 | 967 | 991 | 1014 | 1038 | 1062 | 1086 | 1110 | 1133 | 1157 | 1181
| 6 | 1163 | 1193 | 1224 | 1254 | 1285 | 1315 | 1346 | 1376 | 1406 | 1437 | 1467 | 1498 | 1528
| 6.5 | 1432 | 1469 | 1506 | 1543 | 1580 | 1617 | 1655 | 1692 | 1729 | 1766 | 1803 | 1840 | 1877
| 7 | 1686 | 1730 | 1773 | 1816 | 1860 | 1903 | 1946 | 1990 | 2033 | 2076 | 2119 | 2163 | 2206
| 7.5 | 1919 | 1968 | 2017 | 2066 | 2115 | 2164 | 2213 | 2262 | 2311 | 2360 | 2409 | 2458 | 2507
| 8 | 2137 | 2192 | 2246 | 2301 | 2355 | 2410 | 2464 | 2518 | 2573 | 2627 | 2681 | 2736 | 2791
| 8.5 | 2345 | 2405 | 2464 | 2524 | 2583 | 2643 | 2702 | 2762 | 2821 | 2881 | 2937 | 2986 | 3033
| 9 | 2540 | 2605 | 2669 | 2733 | 2798 | 2862 | 2925 | 2989 | 3039 | 3089 | 3135 | 3173 | 3208
| 9.5 | 2725 | 2794 | 2863 | 2931 | 2998 | 3060 | 3112 | 3163 | 3202 | 3240 | 3275 | 3302 | 3326
| 10 | 2905 | 2974 | 3044 | 3103 | 3158 | 3208 | 3248 | 3288 | 3315 | 3343 | 3366 | 3383 | 3397
| 10.5 | 3071 | 3127 | 3184 | 3231 | 3273 | 3312 | 3340 | 3369 | 3386 | 3403 | 3416 | 3422 | 3426
| 11 | 3196 | 3241 | 3285 | 3321 | 3352 | 3379 | 3397 | 3415 | 3421 | 3427 | 3430 | 3430 | 3430
| 11.5 | 3290 | 3323 | 3356 | 3380 | 3400 | 3417 | 3424 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430
| 12 | 3358 | 3380 | 3402 | 3415 | 3424 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430
| 12.5 | 3403 | 3414 | 3425 | 3429 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430
| 13 | 3427 | 3429 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430
| 13.5 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430
| 14 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430
| 14.5 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430
| 15 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430
| 15.5 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430
| 16 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430
| 16.5 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430
| 17 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430
| 17.5 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430
| 18 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430
| 18.5 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430
| 19 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430
| 19.5 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430
| 20 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430 | 3430

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
TI (%) | 10 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874
| 3.5 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867
| 4 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852
| 4.5 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839
| 5 | 0.829 | 0.829 | 0.829 | 0.829 | 0.829 | 0.829 | 0.829 | 0.829 | 0.829 | 0.829 | 0.829 | 0.829 | 0.829
| 5.5 | 0.797 | 0.797 | 0.797 | 0.797 | 0.797 | 0.797 | 0.797 | 0.797 | 0.797 | 0.797 | 0.797 | 0.797 | 0.797
| 6 | 0.749 | 0.749 | 0.749 | 0.749 | 0.749 | 0.749 | 0.749 | 0.749 | 0.749 | 0.749 | 0.749 | 0.749 | 0.749
| 6.5 | 0.692 | 0.692 | 0.692 | 0.692 | 0.692 | 0.692 | 0.692 | 0.692 | 0.692 | 0.692 | 0.692 | 0.692 | 0.692
| 7 | 0.633 | 0.633 | 0.633 | 0.633 | 0.633 | 0.633 | 0.633 | 0.633 | 0.633 | 0.633 | 0.633 | 0.633 | 0.633
| 7.5 | 0.574 | 0.574 | 0.574 | 0.574 | 0.574 | 0.574 | 0.574 | 0.574 | 0.574 | 0.574 | 0.574 | 0.573 | 0.573
| 8 | 0.514 | 0.514 | 0.514 | 0.514 | 0.514 | 0.514 | 0.514 | 0.514 | 0.513 | 0.513 | 0.512 | 0.511 | 0.51
| 8.5 | 0.457 | 0.457 | 0.457 | 0.457 | 0.457 | 0.457 | 0.456 | 0.455 | 0.454 | 0.453 | 0.451 | 0.449 | 0.447
| 9 | 0.408 | 0.408 | 0.408 | 0.407 | 0.407 | 0.406 | 0.404 | 0.403 | 0.401 | 0.399 | 0.397 | 0.395 | 0.392
| 9.5 | 0.366 | 0.366 | 0.365 | 0.364 | 0.362 | 0.361 | 0.359 | 0.357 | 0.355 | 0.352 | 0.35 | 0.347 | 0.345
| 10 | 0.329 | 0.328 | 0.326 | 0.325 | 0.323 | 0.321 | 0.319 | 0.317 | 0.314 | 0.311 | 0.309 | 0.306 | 0.303
| 10.5 | 0.296 | 0.294 | 0.292 | 0.29 | 0.288 | 0.286 | 0.284 | 0.281 | 0.278 | 0.276 | 0.273 | 0.27 | 0.267
| 11 | 0.266 | 0.264 | 0.262 | 0.26 | 0.258 | 0.255 | 0.253 | 0.25 | 0.247 | 0.244 | 0.241 | 0.238 | 0.235
| 11.5 | 0.24 | 0.238 | 0.236 | 0.233 | 0.231 | 0.228 | 0.225 | 0.223 | 0.22 | 0.217 | 0.214 | 0.211 | 0.207
| 12 | 0.217 | 0.214 | 0.212 | 0.209 | 0.207 | 0.204 | 0.201 | 0.199 | 0.195 | 0.192 | 0.189 | 0.186 | 0.183
| 12.5 | 0.196 | 0.193 | 0.191 | 0.188 | 0.185 | 0.183 | 0.18 | 0.177 | 0.174 | 0.171 | 0.168 | 0.165 | 0.161
| 13 | 0.177 | 0.174 | 0.172 | 0.169 | 0.166 | 0.164 | 0.161 | 0.158 | 0.155 | 0.152 | 0.149 | 0.146 | 0.143
| 13.5 | 0.16 | 0.157 | 0.155 | 0.152 | 0.149 | 0.147 | 0.144 | 0.141 | 0.138 | 0.135 | 0.132 | 0.13 | 0.128
| 14 | 0.145 | 0.142 | 0.14 | 0.137 | 0.134 | 0.132 | 0.129 | 0.126 | 0.123 | 0.121 | 0.119 | 0.117 | 0.114
| 14.5 | 0.132 | 0.129 | 0.126 | 0.124 | 0.121 | 0.118 | 0.116 | 0.113 | 0.111 | 0.109 | 0.107 | 0.105 | 0.103
| 15 | 0.12 | 0.117 | 0.114 | 0.112 | 0.109 | 0.107 | 0.105 | 0.103 | 0.101 | 0.099 | 0.097 | 0.095 | 0.093
| 15.5 | 0.109 | 0.106 | 0.104 | 0.101 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.09 | 0.088 | 0.086 | 0.085
| 16 | 0.099 | 0.097 | 0.094 | 0.092 | 0.09 | 0.089 | 0.087 | 0.085 | 0.083 | 0.082 | 0.08 | 0.079 | 0.077
| 16.5 | 0.091 | 0.089 | 0.087 | 0.085 | 0.083 | 0.081 | 0.08 | 0.078 | 0.076 | 0.075 | 0.074 | 0.072 | 0.071
| 17 | 0.084 | 0.082 | 0.08 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.071 | 0.069 | 0.068 | 0.067 | 0.066
| 17.5 | 0.077 | 0.076 | 0.074 | 0.072 | 0.071 | 0.07 | 0.068 | 0.067 | 0.066 | 0.064 | 0.063 | 0.062 | 0.061
| 18 | 0.072 | 0.071 | 0.069 | 0.068 | 0.066 | 0.065 | 0.064 | 0.063 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057
| 18.5 | 0.068 | 0.066 | 0.065 | 0.064 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054
| 19 | 0.063 | 0.061 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.053 | 0.052 | 0.051 | 0.05
| 19.5 | 0.057 | 0.055 | 0.055 | 0.054 | 0.052 | 0.051 | 0.05 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045
| 20 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.045 | 0.044 | 0.043 | 0.042 | 0.042 | 0.041