## Sheet1
PROPERTIES
General
Name | N175-6.X MW 50-60 Hz vM14_3200
Manufacturer | Nordex
Hub Height | 142 | 179
Power
Rated Power | 3200
Peak Power | 3200
Power Regulation Type | Pitch
Voltage | 950
Rotor
Rotor diameter | 175
Number of blades | 3
Rated RPM | -
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 20
Restart Wind Speed | 19.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -40
Low Temperature Restart | -20
High Temperature Shutdown | 40
High Temperature Restart | 45
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 39.6
Design TI | 0.35

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 49 | 52 | 54 | 57 | 60 | 63 | 65 | 68 | 71 | 74 | 76 | 79 | 82
| 3.5 | 148 | 154 | 159 | 164 | 169 | 174 | 180 | 185 | 190 | 195 | 201 | 206 | 211
| 4 | 283 | 292 | 300 | 309 | 317 | 326 | 335 | 343 | 352 | 360 | 369 | 377 | 386
| 4.5 | 452 | 465 | 477 | 490 | 503 | 516 | 529 | 541 | 554 | 567 | 580 | 593 | 605
| 5 | 655 | 673 | 690 | 708 | 726 | 744 | 762 | 780 | 797 | 815 | 833 | 851 | 869
| 5.5 | 894 | 918 | 942 | 966 | 989 | 1013 | 1037 | 1061 | 1085 | 1108 | 1132 | 1156 | 1180
| 6 | 1152 | 1182 | 1212 | 1242 | 1273 | 1303 | 1333 | 1363 | 1393 | 1423 | 1453 | 1484 | 1514
| 6.5 | 1405 | 1442 | 1478 | 1515 | 1551 | 1587 | 1624 | 1660 | 1697 | 1733 | 1769 | 1806 | 1842
| 7 | 1640 | 1682 | 1724 | 1767 | 1809 | 1851 | 1893 | 1935 | 1978 | 2020 | 2062 | 2104 | 2146
| 7.5 | 1856 | 1903 | 1951 | 1999 | 2046 | 2094 | 2141 | 2189 | 2236 | 2284 | 2331 | 2378 | 2425
| 8 | 2061 | 2114 | 2167 | 2219 | 2272 | 2324 | 2377 | 2429 | 2482 | 2534 | 2587 | 2640 | 2692
| 8.5 | 2255 | 2312 | 2370 | 2427 | 2484 | 2542 | 2599 | 2656 | 2713 | 2767 | 2813 | 2858 | 2903
| 9 | 2437 | 2499 | 2561 | 2623 | 2685 | 2745 | 2804 | 2853 | 2902 | 2946 | 2980 | 3014 | 3048
| 9.5 | 2611 | 2677 | 2742 | 2806 | 2864 | 2915 | 2963 | 3000 | 3038 | 3070 | 3094 | 3118 | 3141
| 10 | 2776 | 2843 | 2900 | 2951 | 2998 | 3037 | 3074 | 3100 | 3128 | 3150 | 3164 | 3178 | 3191
| 10.5 | 2917 | 2971 | 3016 | 3056 | 3092 | 3120 | 3146 | 3162 | 3179 | 3191 | 3195 | 3199 | 3200
| 11 | 3022 | 3064 | 3098 | 3127 | 3153 | 3170 | 3186 | 3191 | 3198 | 3200 | 3200 | 3200 | 3200
| 11.5 | 3099 | 3131 | 3154 | 3173 | 3188 | 3195 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 12 | 3153 | 3174 | 3187 | 3195 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 12.5 | 3186 | 3196 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 13 | 3199 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 13.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 14 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 14.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 15 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 15.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 16 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 16.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 17 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 17.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 18 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 18.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 19 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 19.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 20 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
TI (%) | 10 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874
| 3.5 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867
| 4 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852
| 4.5 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839
| 5 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825
| 5.5 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786
| 6 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734
| 6.5 | 0.674 | 0.674 | 0.674 | 0.674 | 0.674 | 0.674 | 0.674 | 0.674 | 0.674 | 0.674 | 0.674 | 0.674 | 0.674
| 7 | 0.613 | 0.613 | 0.613 | 0.613 | 0.613 | 0.613 | 0.613 | 0.612 | 0.612 | 0.612 | 0.613 | 0.613 | 0.613
| 7.5 | 0.552 | 0.552 | 0.552 | 0.552 | 0.552 | 0.552 | 0.552 | 0.552 | 0.552 | 0.552 | 0.551 | 0.551 | 0.551
| 8 | 0.491 | 0.491 | 0.491 | 0.491 | 0.491 | 0.491 | 0.491 | 0.491 | 0.49 | 0.49 | 0.488 | 0.487 | 0.486
| 8.5 | 0.436 | 0.436 | 0.436 | 0.436 | 0.435 | 0.435 | 0.434 | 0.433 | 0.431 | 0.43 | 0.428 | 0.426 | 0.424
| 9 | 0.389 | 0.389 | 0.388 | 0.387 | 0.387 | 0.385 | 0.384 | 0.382 | 0.38 | 0.378 | 0.376 | 0.373 | 0.371
| 9.5 | 0.348 | 0.348 | 0.346 | 0.345 | 0.344 | 0.342 | 0.34 | 0.338 | 0.336 | 0.333 | 0.331 | 0.328 | 0.325
| 10 | 0.312 | 0.311 | 0.309 | 0.308 | 0.306 | 0.304 | 0.301 | 0.299 | 0.296 | 0.294 | 0.291 | 0.288 | 0.285
| 10.5 | 0.28 | 0.279 | 0.277 | 0.275 | 0.272 | 0.27 | 0.268 | 0.265 | 0.262 | 0.26 | 0.257 | 0.254 | 0.251
| 11 | 0.252 | 0.25 | 0.248 | 0.246 | 0.243 | 0.241 | 0.238 | 0.235 | 0.233 | 0.23 | 0.227 | 0.224 | 0.221
| 11.5 | 0.227 | 0.225 | 0.222 | 0.22 | 0.217 | 0.215 | 0.212 | 0.209 | 0.206 | 0.203 | 0.2 | 0.197 | 0.194
| 12 | 0.204 | 0.202 | 0.199 | 0.197 | 0.194 | 0.192 | 0.189 | 0.186 | 0.183 | 0.18 | 0.177 | 0.174 | 0.171
| 12.5 | 0.184 | 0.182 | 0.179 | 0.176 | 0.174 | 0.171 | 0.168 | 0.165 | 0.162 | 0.159 | 0.156 | 0.153 | 0.15
| 13 | 0.166 | 0.164 | 0.161 | 0.158 | 0.156 | 0.153 | 0.15 | 0.147 | 0.144 | 0.141 | 0.139 | 0.136 | 0.133
| 13.5 | 0.15 | 0.148 | 0.145 | 0.142 | 0.14 | 0.137 | 0.134 | 0.131 | 0.129 | 0.126 | 0.124 | 0.121 | 0.119
| 14 | 0.136 | 0.134 | 0.131 | 0.128 | 0.125 | 0.123 | 0.12 | 0.118 | 0.115 | 0.113 | 0.111 | 0.109 | 0.107
| 14.5 | 0.123 | 0.121 | 0.118 | 0.115 | 0.113 | 0.11 | 0.108 | 0.106 | 0.104 | 0.102 | 0.1 | 0.098 | 0.096
| 15 | 0.112 | 0.109 | 0.107 | 0.104 | 0.102 | 0.1 | 0.098 | 0.096 | 0.094 | 0.092 | 0.091 | 0.089 | 0.087
| 15.5 | 0.102 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.085 | 0.084 | 0.082 | 0.081 | 0.079
| 16 | 0.092 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083 | 0.081 | 0.08 | 0.078 | 0.077 | 0.075 | 0.074 | 0.073
| 16.5 | 0.085 | 0.083 | 0.081 | 0.079 | 0.078 | 0.076 | 0.074 | 0.073 | 0.072 | 0.07 | 0.069 | 0.068 | 0.067
| 17 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.07 | 0.069 | 0.067 | 0.066 | 0.065 | 0.064 | 0.063 | 0.062
| 17.5 | 0.073 | 0.071 | 0.069 | 0.068 | 0.067 | 0.065 | 0.064 | 0.063 | 0.062 | 0.06 | 0.059 | 0.058 | 0.057
| 18 | 0.068 | 0.066 | 0.065 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054
| 18.5 | 0.064 | 0.062 | 0.061 | 0.06 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.051
| 19 | 0.059 | 0.057 | 0.056 | 0.055 | 0.053 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.047
| 19.5 | 0.054 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.044 | 0.043 | 0.043
| 20 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039