## Sheet1
PROPERTIES
General
Name | N175-6.X MW 50-60 Hz vM3_5940_h112
Manufacturer | Nordex
Hub Height | 112
Power
Rated Power | 5940
Peak Power | 5940
Power Regulation Type | Pitch
Voltage | 950
Rotor
Rotor diameter | 175
Number of blades | 3
Rated RPM | -
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 20
Restart Wind Speed | 19.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -40
Low Temperature Restart | -20
High Temperature Shutdown | 40
High Temperature Restart | 45
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 38.5
Design TI | 0.35

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 37 | 40 | 42 | 45 | 48 | 50 | 53 | 56 | 59 | 61 | 64 | 67 | 69 | 72 | 75 | 78 | 80
| 3.5 | 125 | 131 | 136 | 141 | 146 | 151 | 156 | 162 | 167 | 172 | 177 | 182 | 187 | 193 | 198 | 203 | 208
| 4 | 245 | 254 | 262 | 271 | 279 | 288 | 296 | 305 | 313 | 322 | 330 | 339 | 347 | 356 | 364 | 373 | 381
| 4.5 | 396 | 409 | 421 | 434 | 447 | 459 | 472 | 485 | 497 | 510 | 523 | 535 | 548 | 561 | 573 | 586 | 599
| 5 | 577 | 594 | 612 | 630 | 647 | 665 | 683 | 700 | 718 | 736 | 753 | 771 | 789 | 806 | 824 | 842 | 859
| 5.5 | 792 | 815 | 839 | 862 | 886 | 910 | 933 | 957 | 980 | 1004 | 1028 | 1051 | 1075 | 1098 | 1122 | 1146 | 1169
| 6 | 1046 | 1077 | 1107 | 1138 | 1168 | 1199 | 1230 | 1260 | 1291 | 1321 | 1352 | 1383 | 1413 | 1444 | 1474 | 1505 | 1535
| 6.5 | 1345 | 1384 | 1423 | 1462 | 1501 | 1539 | 1578 | 1617 | 1656 | 1695 | 1734 | 1772 | 1811 | 1850 | 1889 | 1927 | 1966
| 7 | 1693 | 1742 | 1790 | 1839 | 1887 | 1936 | 1984 | 2032 | 2081 | 2129 | 2177 | 2226 | 2274 | 2322 | 2370 | 2419 | 2467
| 7.5 | 2093 | 2152 | 2211 | 2271 | 2330 | 2389 | 2449 | 2508 | 2567 | 2626 | 2685 | 2745 | 2804 | 2863 | 2922 | 2981 | 3040
| 8 | 2523 | 2594 | 2665 | 2736 | 2807 | 2878 | 2949 | 3020 | 3091 | 3162 | 3233 | 3304 | 3375 | 3446 | 3516 | 3587 | 3658
| 8.5 | 2958 | 3041 | 3124 | 3207 | 3290 | 3373 | 3455 | 3538 | 3621 | 3704 | 3786 | 3869 | 3951 | 4034 | 4116 | 4199 | 4281
| 9 | 3383 | 3477 | 3572 | 3666 | 3761 | 3855 | 3949 | 4044 | 4138 | 4232 | 4326 | 4421 | 4514 | 4606 | 4699 | 4791 | 4864
| 9.5 | 3783 | 3889 | 3994 | 4099 | 4204 | 4309 | 4415 | 4521 | 4626 | 4728 | 4830 | 4931 | 5016 | 5093 | 5171 | 5248 | 5306
| 10 | 4156 | 4272 | 4387 | 4502 | 4619 | 4735 | 4846 | 4955 | 5064 | 5150 | 5233 | 5317 | 5384 | 5446 | 5507 | 5568 | 5610
| 10.5 | 4510 | 4636 | 4762 | 4886 | 5002 | 5117 | 5213 | 5302 | 5392 | 5460 | 5526 | 5593 | 5644 | 5689 | 5733 | 5778 | 5804
| 11 | 4857 | 4985 | 5106 | 5221 | 5315 | 5410 | 5487 | 5557 | 5629 | 5680 | 5729 | 5778 | 5812 | 5841 | 5870 | 5898 | 5909
| 11.5 | 5169 | 5282 | 5381 | 5475 | 5550 | 5626 | 5685 | 5737 | 5791 | 5825 | 5857 | 5889 | 5907 | 5918 | 5930 | 5940 | 5940
| 12 | 5417 | 5509 | 5589 | 5664 | 5720 | 5778 | 5819 | 5854 | 5891 | 5907 | 5921 | 5936 | 5940 | 5940 | 5940 | 5940 | 5940
| 12.5 | 5609 | 5682 | 5743 | 5798 | 5838 | 5877 | 5900 | 5918 | 5937 | 5939 | 5939 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 13 | 5752 | 5806 | 5849 | 5886 | 5908 | 5930 | 5937 | 5938 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 13.5 | 5852 | 5888 | 5913 | 5932 | 5936 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 14 | 5913 | 5931 | 5937 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 14.5 | 5937 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 15 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 15.5 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 16 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 16.5 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 17 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 17.5 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 18 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 18.5 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 19 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 19.5 | 5926 | 5926 | 5926 | 5926 | 5926 | 5926 | 5926 | 5926 | 5926 | 5926 | 5926 | 5926 | 5926 | 5926 | 5926 | 5926 | 5926
| 20 | 5865 | 5865 | 5865 | 5865 | 5865 | 5865 | 5865 | 5865 | 5865 | 5865 | 5865 | 5865 | 5865 | 5865 | 5865 | 5865 | 5865

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874
| 3.5 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867
| 4 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852
| 4.5 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839
| 5 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83
| 5.5 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824
| 6 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82
| 6.5 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817
| 7 | 0.807 | 0.807 | 0.807 | 0.807 | 0.807 | 0.807 | 0.807 | 0.807 | 0.807 | 0.807 | 0.807 | 0.807 | 0.807 | 0.807 | 0.807 | 0.807 | 0.807
| 7.5 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.783 | 0.783 | 0.784 | 0.784
| 8 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.749
| 8.5 | 0.713 | 0.713 | 0.713 | 0.713 | 0.713 | 0.713 | 0.713 | 0.713 | 0.713 | 0.713 | 0.713 | 0.712 | 0.711 | 0.709 | 0.708 | 0.706 | 0.703
| 9 | 0.671 | 0.671 | 0.671 | 0.671 | 0.671 | 0.671 | 0.67 | 0.67 | 0.669 | 0.668 | 0.666 | 0.664 | 0.662 | 0.659 | 0.657 | 0.653 | 0.649
| 9.5 | 0.627 | 0.627 | 0.627 | 0.627 | 0.626 | 0.626 | 0.624 | 0.622 | 0.62 | 0.617 | 0.615 | 0.612 | 0.608 | 0.605 | 0.602 | 0.598 | 0.593
| 10 | 0.583 | 0.583 | 0.582 | 0.58 | 0.579 | 0.577 | 0.574 | 0.572 | 0.568 | 0.565 | 0.562 | 0.558 | 0.554 | 0.55 | 0.546 | 0.542 | 0.537
| 10.5 | 0.538 | 0.536 | 0.534 | 0.532 | 0.529 | 0.526 | 0.523 | 0.52 | 0.516 | 0.512 | 0.508 | 0.504 | 0.5 | 0.495 | 0.491 | 0.486 | 0.481
| 11 | 0.491 | 0.488 | 0.486 | 0.483 | 0.48 | 0.476 | 0.472 | 0.469 | 0.465 | 0.46 | 0.456 | 0.452 | 0.447 | 0.442 | 0.438 | 0.433 | 0.428
| 11.5 | 0.446 | 0.443 | 0.44 | 0.436 | 0.433 | 0.429 | 0.425 | 0.421 | 0.416 | 0.412 | 0.407 | 0.403 | 0.398 | 0.393 | 0.388 | 0.383 | 0.378
| 12 | 0.405 | 0.402 | 0.398 | 0.394 | 0.39 | 0.386 | 0.382 | 0.377 | 0.373 | 0.368 | 0.363 | 0.359 | 0.353 | 0.348 | 0.344 | 0.338 | 0.333
| 12.5 | 0.368 | 0.364 | 0.36 | 0.356 | 0.352 | 0.348 | 0.343 | 0.339 | 0.334 | 0.329 | 0.324 | 0.319 | 0.314 | 0.309 | 0.304 | 0.299 | 0.294
| 13 | 0.335 | 0.331 | 0.327 | 0.322 | 0.318 | 0.313 | 0.309 | 0.304 | 0.299 | 0.294 | 0.289 | 0.285 | 0.279 | 0.274 | 0.27 | 0.264 | 0.259
| 13.5 | 0.305 | 0.3 | 0.296 | 0.291 | 0.287 | 0.282 | 0.278 | 0.273 | 0.268 | 0.263 | 0.258 | 0.253 | 0.248 | 0.243 | 0.238 | 0.233 | 0.228
| 14 | 0.277 | 0.273 | 0.269 | 0.264 | 0.259 | 0.255 | 0.25 | 0.245 | 0.24 | 0.235 | 0.23 | 0.225 | 0.22 | 0.216 | 0.211 | 0.207 | 0.203
| 14.5 | 0.253 | 0.248 | 0.244 | 0.239 | 0.234 | 0.23 | 0.225 | 0.22 | 0.215 | 0.21 | 0.205 | 0.201 | 0.197 | 0.192 | 0.189 | 0.185 | 0.181
| 15 | 0.231 | 0.226 | 0.221 | 0.217 | 0.212 | 0.207 | 0.202 | 0.198 | 0.193 | 0.189 | 0.184 | 0.18 | 0.177 | 0.173 | 0.17 | 0.166 | 0.163
| 15.5 | 0.21 | 0.206 | 0.201 | 0.196 | 0.192 | 0.187 | 0.182 | 0.178 | 0.174 | 0.17 | 0.166 | 0.163 | 0.159 | 0.156 | 0.153 | 0.15 | 0.147
| 16 | 0.192 | 0.187 | 0.183 | 0.178 | 0.173 | 0.169 | 0.165 | 0.161 | 0.158 | 0.154 | 0.151 | 0.148 | 0.145 | 0.142 | 0.139 | 0.136 | 0.134
| 16.5 | 0.175 | 0.171 | 0.166 | 0.162 | 0.158 | 0.154 | 0.15 | 0.147 | 0.144 | 0.141 | 0.138 | 0.135 | 0.132 | 0.13 | 0.127 | 0.125 | 0.122
| 17 | 0.161 | 0.156 | 0.152 | 0.148 | 0.145 | 0.141 | 0.138 | 0.135 | 0.132 | 0.129 | 0.126 | 0.124 | 0.121 | 0.119 | 0.117 | 0.115 | 0.113
| 17.5 | 0.148 | 0.144 | 0.141 | 0.137 | 0.134 | 0.131 | 0.128 | 0.125 | 0.122 | 0.12 | 0.117 | 0.115 | 0.112 | 0.11 | 0.108 | 0.106 | 0.104
| 18 | 0.138 | 0.134 | 0.131 | 0.127 | 0.124 | 0.122 | 0.119 | 0.116 | 0.114 | 0.111 | 0.109 | 0.107 | 0.105 | 0.103 | 0.101 | 0.099 | 0.097
| 18.5 | 0.129 | 0.125 | 0.122 | 0.119 | 0.116 | 0.114 | 0.111 | 0.109 | 0.107 | 0.104 | 0.102 | 0.1 | 0.098 | 0.096 | 0.095 | 0.093 | 0.091
| 19 | 0.119 | 0.115 | 0.112 | 0.11 | 0.107 | 0.105 | 0.102 | 0.1 | 0.099 | 0.096 | 0.094 | 0.092 | 0.09 | 0.089 | 0.088 | 0.086 | 0.084
| 19.5 | 0.108 | 0.105 | 0.102 | 0.1 | 0.097 | 0.096 | 0.093 | 0.091 | 0.09 | 0.087 | 0.086 | 0.084 | 0.082 | 0.081 | 0.08 | 0.078 | 0.076
| 20 | 0.098 | 0.095 | 0.092 | 0.09 | 0.088 | 0.086 | 0.084 | 0.082 | 0.081 | 0.079 | 0.077 | 0.076 | 0.074 | 0.073 | 0.072 | 0.07 | 0.069