## Sheet1
PROPERTIES
General
Name | N175-6.X MW 50-60 Hz vM3_5940
Manufacturer | Nordex
Hub Height | 142 | 179
Power
Rated Power | 5940
Peak Power | 5940
Power Regulation Type | Pitch
Voltage | 950
Rotor
Rotor diameter | 175
Number of blades | 3
Rated RPM | -
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 20
Restart Wind Speed | 19.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -40
Low Temperature Restart | -20
High Temperature Shutdown | 40
High Temperature Restart | 45
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 39.6
Design TI | 0.35

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 38 | 41 | 43 | 46 | 49 | 52 | 54 | 57 | 60 | 63 | 65 | 68 | 71 | 74 | 76 | 79 | 82
| 3.5 | 127 | 133 | 138 | 143 | 148 | 154 | 159 | 164 | 169 | 174 | 180 | 185 | 190 | 195 | 201 | 206 | 211
| 4 | 249 | 257 | 266 | 274 | 283 | 292 | 300 | 309 | 317 | 326 | 335 | 343 | 352 | 360 | 369 | 378 | 386
| 4.5 | 401 | 413 | 426 | 439 | 452 | 465 | 477 | 490 | 503 | 516 | 529 | 541 | 554 | 567 | 580 | 593 | 605
| 5 | 583 | 601 | 619 | 637 | 655 | 673 | 690 | 708 | 726 | 744 | 762 | 780 | 797 | 815 | 833 | 851 | 869
| 5.5 | 800 | 824 | 848 | 872 | 896 | 919 | 943 | 967 | 991 | 1015 | 1039 | 1062 | 1086 | 1110 | 1134 | 1158 | 1181
| 6 | 1057 | 1088 | 1119 | 1150 | 1181 | 1212 | 1242 | 1273 | 1304 | 1335 | 1366 | 1397 | 1428 | 1458 | 1489 | 1520 | 1551
| 6.5 | 1359 | 1398 | 1437 | 1477 | 1516 | 1555 | 1594 | 1633 | 1672 | 1712 | 1751 | 1790 | 1829 | 1868 | 1907 | 1946 | 1985
| 7 | 1710 | 1759 | 1808 | 1857 | 1906 | 1954 | 2003 | 2052 | 2101 | 2149 | 2198 | 2247 | 2295 | 2344 | 2393 | 2441 | 2490
| 7.5 | 2113 | 2173 | 2232 | 2292 | 2352 | 2412 | 2471 | 2531 | 2591 | 2650 | 2710 | 2770 | 2829 | 2889 | 2948 | 3008 | 3067
| 8 | 2546 | 2618 | 2690 | 2761 | 2833 | 2904 | 2976 | 3047 | 3119 | 3190 | 3262 | 3333 | 3404 | 3475 | 3547 | 3618 | 3689
| 8.5 | 2984 | 3068 | 3152 | 3235 | 3319 | 3402 | 3485 | 3569 | 3652 | 3735 | 3818 | 3901 | 3984 | 4067 | 4150 | 4233 | 4316
| 9 | 3412 | 3507 | 3602 | 3697 | 3792 | 3887 | 3982 | 4077 | 4172 | 4267 | 4361 | 4456 | 4549 | 4642 | 4735 | 4822 | 4893
| 9.5 | 3815 | 3921 | 4027 | 4133 | 4239 | 4344 | 4451 | 4557 | 4662 | 4764 | 4866 | 4967 | 5045 | 5124 | 5201 | 5273 | 5328
| 10 | 4191 | 4306 | 4422 | 4539 | 4656 | 4772 | 4882 | 4991 | 5095 | 5179 | 5262 | 5346 | 5407 | 5469 | 5530 | 5587 | 5626
| 10.5 | 4546 | 4673 | 4800 | 4921 | 5038 | 5152 | 5242 | 5331 | 5416 | 5483 | 5550 | 5616 | 5660 | 5705 | 5750 | 5790 | 5814
| 11 | 4895 | 5020 | 5142 | 5250 | 5344 | 5438 | 5509 | 5580 | 5647 | 5697 | 5746 | 5794 | 5823 | 5852 | 5880 | 5905 | 5913
| 11.5 | 5204 | 5309 | 5410 | 5497 | 5573 | 5648 | 5701 | 5754 | 5803 | 5836 | 5868 | 5900 | 5911 | 5923 | 5934 | 5940 | 5940
| 12 | 5446 | 5532 | 5612 | 5680 | 5738 | 5794 | 5830 | 5865 | 5897 | 5912 | 5926 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 12.5 | 5632 | 5699 | 5760 | 5810 | 5849 | 5887 | 5906 | 5924 | 5938 | 5939 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 13 | 5770 | 5818 | 5861 | 5893 | 5914 | 5935 | 5937 | 5939 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 13.5 | 5865 | 5895 | 5919 | 5934 | 5938 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 14 | 5921 | 5933 | 5939 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 14.5 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 15 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 15.5 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 16 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 16.5 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 17 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 17.5 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 18 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 18.5 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 19 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940 | 5940
| 19.5 | 5926 | 5926 | 5926 | 5926 | 5926 | 5926 | 5926 | 5926 | 5926 | 5926 | 5926 | 5926 | 5926 | 5926 | 5926 | 5926 | 5926
| 20 | 5865 | 5865 | 5865 | 5865 | 5865 | 5865 | 5865 | 5865 | 5865 | 5865 | 5865 | 5865 | 5865 | 5865 | 5865 | 5865 | 5865

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874
| 3.5 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867
| 4 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852
| 4.5 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839
| 5 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83
| 5.5 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824
| 6 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82
| 6.5 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817
| 7 | 0.807 | 0.807 | 0.807 | 0.807 | 0.807 | 0.807 | 0.807 | 0.807 | 0.807 | 0.807 | 0.807 | 0.807 | 0.807 | 0.807 | 0.807 | 0.807 | 0.807
| 7.5 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.784 | 0.783 | 0.783 | 0.783 | 0.784
| 8 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.75
| 8.5 | 0.713 | 0.713 | 0.713 | 0.713 | 0.713 | 0.713 | 0.713 | 0.713 | 0.713 | 0.713 | 0.713 | 0.713 | 0.711 | 0.71 | 0.709 | 0.707 | 0.704
| 9 | 0.671 | 0.671 | 0.671 | 0.671 | 0.671 | 0.671 | 0.671 | 0.67 | 0.67 | 0.668 | 0.667 | 0.665 | 0.662 | 0.66 | 0.657 | 0.655 | 0.651
| 9.5 | 0.627 | 0.627 | 0.627 | 0.627 | 0.627 | 0.626 | 0.624 | 0.623 | 0.621 | 0.618 | 0.616 | 0.613 | 0.61 | 0.606 | 0.603 | 0.599 | 0.595
| 10 | 0.583 | 0.583 | 0.582 | 0.581 | 0.579 | 0.577 | 0.575 | 0.572 | 0.57 | 0.566 | 0.563 | 0.56 | 0.555 | 0.551 | 0.548 | 0.544 | 0.539
| 10.5 | 0.538 | 0.536 | 0.535 | 0.532 | 0.53 | 0.527 | 0.524 | 0.521 | 0.517 | 0.513 | 0.51 | 0.506 | 0.501 | 0.497 | 0.493 | 0.488 | 0.483
| 11 | 0.492 | 0.489 | 0.487 | 0.484 | 0.481 | 0.477 | 0.474 | 0.47 | 0.466 | 0.462 | 0.458 | 0.454 | 0.449 | 0.444 | 0.439 | 0.435 | 0.429
| 11.5 | 0.447 | 0.444 | 0.441 | 0.437 | 0.434 | 0.43 | 0.426 | 0.422 | 0.418 | 0.413 | 0.409 | 0.405 | 0.399 | 0.394 | 0.39 | 0.385 | 0.38
| 12 | 0.406 | 0.403 | 0.399 | 0.395 | 0.391 | 0.387 | 0.383 | 0.379 | 0.374 | 0.369 | 0.365 | 0.36 | 0.355 | 0.35 | 0.345 | 0.341 | 0.335
| 12.5 | 0.369 | 0.365 | 0.361 | 0.357 | 0.353 | 0.349 | 0.344 | 0.34 | 0.335 | 0.331 | 0.326 | 0.321 | 0.316 | 0.311 | 0.306 | 0.301 | 0.296
| 13 | 0.336 | 0.332 | 0.328 | 0.323 | 0.319 | 0.315 | 0.31 | 0.305 | 0.301 | 0.296 | 0.291 | 0.286 | 0.281 | 0.276 | 0.271 | 0.266 | 0.261
| 13.5 | 0.306 | 0.301 | 0.297 | 0.293 | 0.288 | 0.284 | 0.279 | 0.274 | 0.27 | 0.265 | 0.26 | 0.255 | 0.25 | 0.245 | 0.24 | 0.235 | 0.23
| 14 | 0.279 | 0.274 | 0.27 | 0.265 | 0.261 | 0.256 | 0.251 | 0.246 | 0.242 | 0.237 | 0.232 | 0.227 | 0.222 | 0.217 | 0.213 | 0.208 | 0.204
| 14.5 | 0.254 | 0.249 | 0.245 | 0.24 | 0.236 | 0.231 | 0.226 | 0.221 | 0.217 | 0.212 | 0.207 | 0.202 | 0.198 | 0.194 | 0.19 | 0.186 | 0.183
| 15 | 0.232 | 0.227 | 0.223 | 0.218 | 0.213 | 0.209 | 0.204 | 0.199 | 0.194 | 0.19 | 0.186 | 0.182 | 0.178 | 0.174 | 0.171 | 0.167 | 0.164
| 15.5 | 0.212 | 0.207 | 0.202 | 0.198 | 0.193 | 0.188 | 0.184 | 0.179 | 0.175 | 0.171 | 0.168 | 0.164 | 0.161 | 0.157 | 0.154 | 0.151 | 0.148
| 16 | 0.193 | 0.188 | 0.184 | 0.179 | 0.175 | 0.17 | 0.166 | 0.162 | 0.159 | 0.155 | 0.152 | 0.149 | 0.146 | 0.143 | 0.14 | 0.137 | 0.135
| 16.5 | 0.177 | 0.172 | 0.167 | 0.163 | 0.159 | 0.155 | 0.151 | 0.148 | 0.145 | 0.142 | 0.139 | 0.136 | 0.133 | 0.13 | 0.128 | 0.126 | 0.123
| 17 | 0.162 | 0.158 | 0.153 | 0.15 | 0.146 | 0.142 | 0.139 | 0.136 | 0.133 | 0.13 | 0.127 | 0.125 | 0.122 | 0.12 | 0.118 | 0.116 | 0.113
| 17.5 | 0.149 | 0.145 | 0.142 | 0.138 | 0.135 | 0.132 | 0.129 | 0.126 | 0.123 | 0.12 | 0.118 | 0.115 | 0.113 | 0.111 | 0.109 | 0.107 | 0.105
| 18 | 0.139 | 0.135 | 0.132 | 0.128 | 0.125 | 0.122 | 0.12 | 0.117 | 0.114 | 0.112 | 0.11 | 0.108 | 0.106 | 0.104 | 0.102 | 0.1 | 0.098
| 18.5 | 0.13 | 0.126 | 0.123 | 0.12 | 0.117 | 0.115 | 0.112 | 0.11 | 0.107 | 0.105 | 0.103 | 0.101 | 0.099 | 0.097 | 0.095 | 0.094 | 0.092
| 19 | 0.12 | 0.116 | 0.113 | 0.111 | 0.108 | 0.106 | 0.103 | 0.101 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.088 | 0.087 | 0.085
| 19.5 | 0.109 | 0.106 | 0.103 | 0.101 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083 | 0.081 | 0.08 | 0.079 | 0.077
| 20 | 0.098 | 0.095 | 0.093 | 0.091 | 0.088 | 0.087 | 0.085 | 0.083 | 0.081 | 0.079 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.071 | 0.07