## Sheet1
PROPERTIES
General
Name | N175-6.X MW 50-60 Hz vM4_5800_h112
Manufacturer | Nordex
Hub Height | 112
Power
Rated Power | 5800
Peak Power | 5800
Power Regulation Type | Pitch
Voltage | 950
Rotor
Rotor diameter | 175
Number of blades | 3
Rated RPM | -
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 20
Restart Wind Speed | 19.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -40
Low Temperature Restart | -20
High Temperature Shutdown | 40
High Temperature Restart | 45
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 38.5
Design TI | 0.35

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 37 | 40 | 42 | 45 | 48 | 50 | 53 | 56 | 59 | 61 | 64 | 67 | 69 | 72 | 75 | 78 | 80
| 3.5 | 125 | 131 | 136 | 141 | 146 | 151 | 156 | 162 | 167 | 172 | 177 | 182 | 187 | 193 | 198 | 203 | 208
| 4 | 245 | 254 | 262 | 271 | 279 | 288 | 296 | 305 | 313 | 322 | 330 | 339 | 347 | 356 | 364 | 373 | 381
| 4.5 | 396 | 409 | 421 | 434 | 447 | 459 | 472 | 485 | 497 | 510 | 523 | 535 | 548 | 561 | 573 | 586 | 599
| 5 | 577 | 594 | 612 | 630 | 647 | 665 | 683 | 700 | 718 | 736 | 753 | 771 | 789 | 806 | 824 | 842 | 859
| 5.5 | 792 | 815 | 839 | 862 | 886 | 910 | 933 | 957 | 980 | 1004 | 1028 | 1051 | 1075 | 1098 | 1122 | 1146 | 1169
| 6 | 1046 | 1077 | 1107 | 1138 | 1168 | 1199 | 1230 | 1260 | 1291 | 1322 | 1352 | 1383 | 1413 | 1444 | 1474 | 1505 | 1535
| 6.5 | 1345 | 1384 | 1423 | 1462 | 1501 | 1539 | 1578 | 1617 | 1656 | 1695 | 1733 | 1772 | 1811 | 1850 | 1889 | 1927 | 1966
| 7 | 1694 | 1742 | 1791 | 1839 | 1887 | 1936 | 1984 | 2033 | 2081 | 2129 | 2178 | 2226 | 2274 | 2323 | 2371 | 2419 | 2467
| 7.5 | 2088 | 2148 | 2207 | 2266 | 2325 | 2385 | 2444 | 2503 | 2562 | 2621 | 2680 | 2739 | 2798 | 2857 | 2916 | 2975 | 3034
| 8 | 2504 | 2574 | 2645 | 2716 | 2786 | 2857 | 2927 | 2998 | 3068 | 3139 | 3209 | 3279 | 3349 | 3420 | 3490 | 3560 | 3630
| 8.5 | 2918 | 3000 | 3082 | 3163 | 3245 | 3327 | 3409 | 3491 | 3572 | 3654 | 3735 | 3817 | 3898 | 3980 | 4061 | 4142 | 4224
| 9 | 3316 | 3408 | 3501 | 3594 | 3687 | 3779 | 3872 | 3964 | 4056 | 4149 | 4241 | 4334 | 4426 | 4517 | 4607 | 4698 | 4778
| 9.5 | 3688 | 3791 | 3894 | 3996 | 4099 | 4201 | 4304 | 4407 | 4510 | 4611 | 4710 | 4809 | 4902 | 4978 | 5054 | 5130 | 5194
| 10 | 4037 | 4149 | 4261 | 4373 | 4486 | 4599 | 4710 | 4816 | 4922 | 5015 | 5097 | 5178 | 5253 | 5314 | 5373 | 5433 | 5481
| 10.5 | 4372 | 4493 | 4615 | 4738 | 4851 | 4963 | 5067 | 5153 | 5240 | 5315 | 5380 | 5445 | 5503 | 5547 | 5590 | 5634 | 5667
| 11 | 4696 | 4827 | 4947 | 5065 | 5159 | 5251 | 5335 | 5403 | 5473 | 5530 | 5578 | 5626 | 5668 | 5696 | 5723 | 5752 | 5769
| 11.5 | 4997 | 5119 | 5220 | 5316 | 5392 | 5465 | 5532 | 5582 | 5634 | 5675 | 5706 | 5738 | 5764 | 5775 | 5786 | 5798 | 5800
| 12 | 5246 | 5346 | 5429 | 5506 | 5564 | 5620 | 5668 | 5702 | 5737 | 5761 | 5776 | 5791 | 5800 | 5800 | 5800 | 5800 | 5800
| 12.5 | 5440 | 5521 | 5586 | 5645 | 5685 | 5723 | 5755 | 5772 | 5790 | 5798 | 5799 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800
| 13 | 5587 | 5650 | 5696 | 5737 | 5760 | 5781 | 5796 | 5798 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800
| 13.5 | 5691 | 5736 | 5765 | 5788 | 5795 | 5799 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800
| 14 | 5756 | 5784 | 5795 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800
| 14.5 | 5790 | 5799 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800
| 15 | 5800 | 5799 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800
| 15.5 | 5800 | 5799 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800
| 16 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800
| 16.5 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800
| 17 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800
| 17.5 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800
| 18 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800
| 18.5 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800
| 19 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800
| 19.5 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800
| 20 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874
| 3.5 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867
| 4 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852
| 4.5 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839
| 5 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83
| 5.5 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824
| 6 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82
| 6.5 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817 | 0.817
| 7 | 0.802 | 0.802 | 0.802 | 0.802 | 0.802 | 0.802 | 0.802 | 0.802 | 0.802 | 0.802 | 0.802 | 0.802 | 0.802 | 0.802 | 0.802 | 0.802 | 0.802
| 7.5 | 0.774 | 0.774 | 0.774 | 0.774 | 0.774 | 0.774 | 0.774 | 0.774 | 0.774 | 0.774 | 0.774 | 0.774 | 0.774 | 0.774 | 0.774 | 0.774 | 0.774
| 8 | 0.738 | 0.738 | 0.738 | 0.738 | 0.738 | 0.738 | 0.738 | 0.738 | 0.738 | 0.738 | 0.738 | 0.738 | 0.738 | 0.739 | 0.739 | 0.738 | 0.737
| 8.5 | 0.697 | 0.697 | 0.697 | 0.697 | 0.697 | 0.697 | 0.697 | 0.697 | 0.697 | 0.697 | 0.697 | 0.697 | 0.696 | 0.695 | 0.694 | 0.692 | 0.689
| 9 | 0.654 | 0.654 | 0.654 | 0.654 | 0.654 | 0.654 | 0.654 | 0.653 | 0.653 | 0.651 | 0.65 | 0.649 | 0.646 | 0.644 | 0.641 | 0.639 | 0.635
| 9.5 | 0.609 | 0.609 | 0.609 | 0.609 | 0.608 | 0.608 | 0.606 | 0.605 | 0.603 | 0.601 | 0.598 | 0.596 | 0.593 | 0.589 | 0.586 | 0.583 | 0.579
| 10 | 0.564 | 0.564 | 0.563 | 0.562 | 0.56 | 0.559 | 0.556 | 0.554 | 0.551 | 0.548 | 0.545 | 0.542 | 0.538 | 0.534 | 0.531 | 0.527 | 0.522
| 10.5 | 0.518 | 0.517 | 0.515 | 0.513 | 0.511 | 0.508 | 0.505 | 0.502 | 0.499 | 0.495 | 0.492 | 0.488 | 0.484 | 0.48 | 0.476 | 0.471 | 0.467
| 11 | 0.472 | 0.47 | 0.467 | 0.465 | 0.461 | 0.459 | 0.455 | 0.451 | 0.448 | 0.444 | 0.44 | 0.436 | 0.431 | 0.427 | 0.422 | 0.418 | 0.413
| 11.5 | 0.428 | 0.426 | 0.423 | 0.42 | 0.416 | 0.413 | 0.409 | 0.405 | 0.401 | 0.397 | 0.392 | 0.388 | 0.383 | 0.379 | 0.374 | 0.37 | 0.365
| 12 | 0.389 | 0.386 | 0.383 | 0.38 | 0.376 | 0.372 | 0.368 | 0.364 | 0.36 | 0.355 | 0.351 | 0.346 | 0.341 | 0.337 | 0.332 | 0.327 | 0.322
| 12.5 | 0.354 | 0.351 | 0.347 | 0.343 | 0.339 | 0.335 | 0.331 | 0.327 | 0.323 | 0.318 | 0.313 | 0.309 | 0.304 | 0.299 | 0.295 | 0.29 | 0.285
| 13 | 0.323 | 0.319 | 0.315 | 0.311 | 0.307 | 0.303 | 0.298 | 0.294 | 0.289 | 0.285 | 0.28 | 0.276 | 0.271 | 0.266 | 0.261 | 0.256 | 0.251
| 13.5 | 0.294 | 0.29 | 0.286 | 0.282 | 0.277 | 0.273 | 0.269 | 0.264 | 0.26 | 0.255 | 0.25 | 0.246 | 0.241 | 0.236 | 0.231 | 0.227 | 0.222
| 14 | 0.268 | 0.264 | 0.26 | 0.255 | 0.251 | 0.247 | 0.242 | 0.238 | 0.233 | 0.228 | 0.224 | 0.219 | 0.214 | 0.21 | 0.205 | 0.201 | 0.197
| 14.5 | 0.244 | 0.24 | 0.236 | 0.232 | 0.227 | 0.223 | 0.218 | 0.214 | 0.209 | 0.204 | 0.2 | 0.196 | 0.191 | 0.187 | 0.183 | 0.18 | 0.176
| 15 | 0.223 | 0.219 | 0.215 | 0.21 | 0.206 | 0.202 | 0.197 | 0.192 | 0.188 | 0.184 | 0.179 | 0.176 | 0.172 | 0.168 | 0.165 | 0.162 | 0.159
| 15.5 | 0.204 | 0.2 | 0.195 | 0.191 | 0.186 | 0.182 | 0.178 | 0.173 | 0.169 | 0.166 | 0.162 | 0.159 | 0.155 | 0.152 | 0.149 | 0.146 | 0.144
| 16 | 0.186 | 0.182 | 0.178 | 0.173 | 0.169 | 0.165 | 0.161 | 0.157 | 0.153 | 0.15 | 0.147 | 0.144 | 0.141 | 0.138 | 0.135 | 0.133 | 0.13
| 16.5 | 0.17 | 0.166 | 0.162 | 0.158 | 0.154 | 0.15 | 0.147 | 0.143 | 0.14 | 0.137 | 0.134 | 0.131 | 0.129 | 0.126 | 0.124 | 0.121 | 0.119
| 17 | 0.157 | 0.152 | 0.148 | 0.145 | 0.141 | 0.138 | 0.135 | 0.131 | 0.129 | 0.126 | 0.123 | 0.121 | 0.118 | 0.116 | 0.114 | 0.112 | 0.11
| 17.5 | 0.144 | 0.141 | 0.137 | 0.134 | 0.13 | 0.127 | 0.124 | 0.122 | 0.119 | 0.116 | 0.114 | 0.112 | 0.11 | 0.108 | 0.106 | 0.104 | 0.102
| 18 | 0.134 | 0.131 | 0.127 | 0.124 | 0.121 | 0.118 | 0.116 | 0.113 | 0.111 | 0.108 | 0.106 | 0.104 | 0.102 | 0.1 | 0.098 | 0.097 | 0.095
| 18.5 | 0.126 | 0.122 | 0.119 | 0.116 | 0.114 | 0.111 | 0.108 | 0.106 | 0.104 | 0.102 | 0.1 | 0.098 | 0.096 | 0.094 | 0.092 | 0.091 | 0.089
| 19 | 0.116 | 0.112 | 0.11 | 0.107 | 0.105 | 0.102 | 0.1 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.089 | 0.087 | 0.085 | 0.084 | 0.082
| 19.5 | 0.106 | 0.102 | 0.1 | 0.097 | 0.096 | 0.093 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084 | 0.082 | 0.081 | 0.079 | 0.077 | 0.076 | 0.075
| 20 | 0.095 | 0.092 | 0.09 | 0.088 | 0.086 | 0.084 | 0.082 | 0.08 | 0.079 | 0.077 | 0.076 | 0.074 | 0.073 | 0.071 | 0.07 | 0.069 | 0.067