## Sheet1
PROPERTIES
General
Name | N175-6.X MW 50-60 Hz vM6_5560
Manufacturer | Nordex
Hub Height | 142 | 179
Power
Rated Power | 5560
Peak Power | 5560
Power Regulation Type | Pitch
Voltage | 950
Rotor
Rotor diameter | 175
Number of blades | 3
Rated RPM | -
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 20
Restart Wind Speed | 19.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -40
Low Temperature Restart | -20
High Temperature Shutdown | 40
High Temperature Restart | 45
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 39.6
Design TI | 0.35

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 38 | 41 | 43 | 46 | 49 | 52 | 54 | 57 | 60 | 63 | 65 | 68 | 71 | 74 | 76 | 79 | 82
| 3.5 | 127 | 133 | 138 | 143 | 148 | 154 | 159 | 164 | 169 | 174 | 180 | 185 | 190 | 195 | 201 | 206 | 211
| 4 | 249 | 257 | 266 | 274 | 283 | 292 | 300 | 309 | 317 | 326 | 335 | 343 | 352 | 360 | 369 | 378 | 386
| 4.5 | 401 | 413 | 426 | 439 | 452 | 465 | 477 | 490 | 503 | 516 | 529 | 541 | 554 | 567 | 580 | 593 | 605
| 5 | 583 | 601 | 619 | 637 | 655 | 673 | 690 | 708 | 726 | 744 | 762 | 780 | 797 | 815 | 833 | 851 | 869
| 5.5 | 800 | 824 | 848 | 872 | 896 | 919 | 943 | 967 | 991 | 1015 | 1039 | 1062 | 1086 | 1110 | 1134 | 1158 | 1181
| 6 | 1057 | 1088 | 1119 | 1150 | 1181 | 1212 | 1242 | 1273 | 1304 | 1335 | 1366 | 1397 | 1428 | 1458 | 1489 | 1520 | 1551
| 6.5 | 1359 | 1398 | 1437 | 1477 | 1516 | 1555 | 1594 | 1633 | 1673 | 1712 | 1751 | 1790 | 1829 | 1868 | 1907 | 1946 | 1985
| 7 | 1709 | 1758 | 1807 | 1856 | 1904 | 1953 | 2002 | 2051 | 2099 | 2148 | 2197 | 2245 | 2294 | 2343 | 2391 | 2440 | 2488
| 7.5 | 2091 | 2150 | 2209 | 2269 | 2328 | 2387 | 2446 | 2505 | 2564 | 2623 | 2683 | 2742 | 2801 | 2859 | 2918 | 2977 | 3036
| 8 | 2477 | 2547 | 2617 | 2686 | 2756 | 2826 | 2896 | 2965 | 3035 | 3104 | 3174 | 3243 | 3312 | 3382 | 3451 | 3521 | 3590
| 8.5 | 2853 | 2933 | 3013 | 3093 | 3172 | 3252 | 3332 | 3412 | 3491 | 3571 | 3651 | 3730 | 3810 | 3889 | 3969 | 4048 | 4127
| 9 | 3204 | 3294 | 3384 | 3473 | 3562 | 3652 | 3741 | 3830 | 3919 | 4008 | 4098 | 4187 | 4276 | 4364 | 4452 | 4539 | 4626
| 9.5 | 3532 | 3630 | 3728 | 3827 | 3925 | 4023 | 4121 | 4219 | 4318 | 4416 | 4511 | 4606 | 4700 | 4781 | 4854 | 4925 | 4998
| 10 | 3844 | 3951 | 4058 | 4165 | 4271 | 4378 | 4486 | 4588 | 4689 | 4790 | 4870 | 4947 | 5024 | 5088 | 5145 | 5201 | 5259
| 10.5 | 4146 | 4261 | 4376 | 4491 | 4607 | 4714 | 4820 | 4908 | 4990 | 5073 | 5136 | 5198 | 5258 | 5307 | 5348 | 5388 | 5430
| 11 | 4431 | 4554 | 4678 | 4793 | 4903 | 4992 | 5079 | 5148 | 5213 | 5279 | 5326 | 5372 | 5416 | 5449 | 5476 | 5501 | 5528
| 11.5 | 4705 | 4828 | 4943 | 5040 | 5131 | 5202 | 5273 | 5325 | 5373 | 5423 | 5454 | 5484 | 5512 | 5530 | 5541 | 5550 | 5560
| 12 | 4950 | 5057 | 5152 | 5231 | 5304 | 5359 | 5412 | 5448 | 5480 | 5514 | 5529 | 5543 | 5555 | 5560 | 5560 | 5559 | 5560
| 12.5 | 5147 | 5235 | 5311 | 5373 | 5428 | 5466 | 5503 | 5523 | 5539 | 5557 | 5559 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560
| 13 | 5297 | 5367 | 5426 | 5470 | 5509 | 5531 | 5552 | 5556 | 5558 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560
| 13.5 | 5406 | 5459 | 5501 | 5528 | 5551 | 5557 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560
| 14 | 5482 | 5518 | 5543 | 5555 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560
| 14.5 | 5532 | 5551 | 5559 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560
| 15 | 5555 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560
| 15.5 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560
| 16 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560
| 16.5 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560
| 17 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560
| 17.5 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560
| 18 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560
| 18.5 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560
| 19 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560
| 19.5 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560
| 20 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560 | 5560

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874
| 3.5 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867
| 4 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852
| 4.5 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839
| 5 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83
| 5.5 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824
| 6 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82
| 6.5 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81
| 7 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786
| 7.5 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751 | 0.751
| 8 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71
| 8.5 | 0.665 | 0.665 | 0.665 | 0.665 | 0.665 | 0.665 | 0.665 | 0.665 | 0.665 | 0.665 | 0.665 | 0.665 | 0.665 | 0.664 | 0.663 | 0.662 | 0.661
| 9 | 0.618 | 0.618 | 0.618 | 0.618 | 0.618 | 0.618 | 0.618 | 0.618 | 0.618 | 0.618 | 0.617 | 0.616 | 0.614 | 0.612 | 0.61 | 0.608 | 0.606
| 9.5 | 0.572 | 0.572 | 0.572 | 0.572 | 0.572 | 0.571 | 0.571 | 0.57 | 0.568 | 0.567 | 0.565 | 0.563 | 0.561 | 0.558 | 0.555 | 0.552 | 0.55
| 10 | 0.525 | 0.525 | 0.525 | 0.524 | 0.524 | 0.522 | 0.521 | 0.519 | 0.517 | 0.515 | 0.512 | 0.509 | 0.506 | 0.503 | 0.5 | 0.496 | 0.493
| 10.5 | 0.479 | 0.478 | 0.478 | 0.477 | 0.475 | 0.473 | 0.471 | 0.468 | 0.465 | 0.463 | 0.459 | 0.456 | 0.453 | 0.449 | 0.446 | 0.442 | 0.439
| 11 | 0.436 | 0.435 | 0.434 | 0.432 | 0.43 | 0.427 | 0.424 | 0.421 | 0.418 | 0.415 | 0.411 | 0.408 | 0.404 | 0.4 | 0.396 | 0.392 | 0.389
| 11.5 | 0.397 | 0.395 | 0.393 | 0.391 | 0.388 | 0.385 | 0.382 | 0.379 | 0.375 | 0.372 | 0.368 | 0.364 | 0.361 | 0.357 | 0.352 | 0.348 | 0.345
| 12 | 0.362 | 0.36 | 0.357 | 0.355 | 0.352 | 0.348 | 0.345 | 0.341 | 0.338 | 0.334 | 0.33 | 0.326 | 0.322 | 0.318 | 0.314 | 0.31 | 0.306
| 12.5 | 0.33 | 0.328 | 0.325 | 0.322 | 0.319 | 0.315 | 0.311 | 0.308 | 0.304 | 0.3 | 0.296 | 0.292 | 0.288 | 0.284 | 0.279 | 0.275 | 0.271
| 13 | 0.301 | 0.298 | 0.295 | 0.292 | 0.289 | 0.285 | 0.281 | 0.277 | 0.273 | 0.27 | 0.265 | 0.261 | 0.257 | 0.253 | 0.248 | 0.244 | 0.24
| 13.5 | 0.275 | 0.272 | 0.269 | 0.265 | 0.262 | 0.258 | 0.254 | 0.25 | 0.246 | 0.242 | 0.238 | 0.234 | 0.23 | 0.226 | 0.221 | 0.217 | 0.213
| 14 | 0.252 | 0.248 | 0.245 | 0.242 | 0.238 | 0.234 | 0.23 | 0.226 | 0.222 | 0.218 | 0.214 | 0.209 | 0.205 | 0.201 | 0.197 | 0.193 | 0.189
| 14.5 | 0.23 | 0.227 | 0.224 | 0.22 | 0.216 | 0.212 | 0.208 | 0.204 | 0.2 | 0.196 | 0.192 | 0.188 | 0.184 | 0.18 | 0.176 | 0.173 | 0.169
| 15 | 0.211 | 0.207 | 0.204 | 0.2 | 0.197 | 0.192 | 0.189 | 0.184 | 0.18 | 0.176 | 0.172 | 0.169 | 0.165 | 0.162 | 0.159 | 0.155 | 0.153
| 15.5 | 0.193 | 0.19 | 0.186 | 0.182 | 0.179 | 0.174 | 0.171 | 0.167 | 0.163 | 0.159 | 0.156 | 0.152 | 0.149 | 0.146 | 0.143 | 0.141 | 0.138
| 16 | 0.177 | 0.173 | 0.17 | 0.166 | 0.162 | 0.158 | 0.155 | 0.151 | 0.147 | 0.144 | 0.141 | 0.138 | 0.135 | 0.133 | 0.13 | 0.128 | 0.125
| 16.5 | 0.163 | 0.159 | 0.155 | 0.152 | 0.148 | 0.144 | 0.141 | 0.138 | 0.135 | 0.132 | 0.129 | 0.126 | 0.124 | 0.121 | 0.119 | 0.117 | 0.115
| 17 | 0.15 | 0.146 | 0.143 | 0.139 | 0.136 | 0.132 | 0.129 | 0.126 | 0.124 | 0.121 | 0.119 | 0.116 | 0.114 | 0.112 | 0.11 | 0.108 | 0.106
| 17.5 | 0.139 | 0.135 | 0.132 | 0.128 | 0.125 | 0.122 | 0.12 | 0.117 | 0.114 | 0.112 | 0.11 | 0.108 | 0.105 | 0.103 | 0.101 | 0.1 | 0.098
| 18 | 0.129 | 0.126 | 0.123 | 0.12 | 0.117 | 0.114 | 0.111 | 0.109 | 0.107 | 0.104 | 0.102 | 0.1 | 0.098 | 0.096 | 0.095 | 0.093 | 0.091
| 18.5 | 0.121 | 0.118 | 0.115 | 0.112 | 0.109 | 0.107 | 0.104 | 0.102 | 0.1 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.089 | 0.087 | 0.086
| 19 | 0.112 | 0.109 | 0.106 | 0.103 | 0.1 | 0.099 | 0.096 | 0.094 | 0.092 | 0.09 | 0.089 | 0.087 | 0.085 | 0.083 | 0.082 | 0.08 | 0.079
| 19.5 | 0.102 | 0.099 | 0.096 | 0.094 | 0.091 | 0.09 | 0.087 | 0.086 | 0.084 | 0.082 | 0.081 | 0.079 | 0.077 | 0.076 | 0.075 | 0.073 | 0.072
| 20 | 0.091 | 0.089 | 0.087 | 0.085 | 0.082 | 0.081 | 0.079 | 0.077 | 0.076 | 0.074 | 0.073 | 0.071 | 0.07 | 0.068 | 0.067 | 0.066 | 0.065