## Sheet1
PROPERTIES
General
Name | N175-6.X MW 50-60 Hz vM7_5030_h112
Manufacturer | Nordex
Hub Height | 112
Power
Rated Power | 5030
Peak Power | 5030
Power Regulation Type | Pitch
Voltage | 950
Rotor
Rotor diameter | 175
Number of blades | 3
Rated RPM | -
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 20
Restart Wind Speed | 19.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -40
Low Temperature Restart | -20
High Temperature Shutdown | 40
High Temperature Restart | 45
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 38.5
Design TI | 0.35

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 37 | 40 | 42 | 45 | 48 | 50 | 53 | 56 | 59 | 61 | 64 | 67 | 69 | 72 | 75 | 78 | 80
| 3.5 | 125 | 131 | 136 | 141 | 146 | 151 | 156 | 162 | 167 | 172 | 177 | 182 | 187 | 193 | 198 | 203 | 208
| 4 | 245 | 254 | 262 | 271 | 279 | 288 | 296 | 305 | 313 | 322 | 330 | 339 | 347 | 356 | 364 | 373 | 381
| 4.5 | 396 | 409 | 421 | 434 | 447 | 459 | 472 | 485 | 497 | 510 | 523 | 535 | 548 | 561 | 573 | 586 | 599
| 5 | 577 | 594 | 612 | 630 | 647 | 665 | 683 | 700 | 718 | 736 | 753 | 771 | 789 | 806 | 824 | 842 | 859
| 5.5 | 792 | 815 | 839 | 862 | 886 | 910 | 933 | 957 | 980 | 1004 | 1028 | 1051 | 1075 | 1098 | 1122 | 1145 | 1169
| 6 | 1046 | 1077 | 1107 | 1138 | 1169 | 1199 | 1230 | 1261 | 1291 | 1322 | 1352 | 1383 | 1414 | 1444 | 1475 | 1505 | 1536
| 6.5 | 1342 | 1380 | 1419 | 1458 | 1497 | 1536 | 1574 | 1613 | 1652 | 1690 | 1729 | 1768 | 1807 | 1845 | 1884 | 1923 | 1961
| 7 | 1656 | 1704 | 1751 | 1798 | 1846 | 1893 | 1941 | 1988 | 2035 | 2083 | 2130 | 2177 | 2224 | 2272 | 2319 | 2366 | 2413
| 7.5 | 1968 | 2024 | 2080 | 2136 | 2192 | 2248 | 2304 | 2360 | 2416 | 2472 | 2528 | 2583 | 2639 | 2695 | 2751 | 2806 | 2862
| 8 | 2263 | 2327 | 2391 | 2455 | 2519 | 2583 | 2647 | 2711 | 2775 | 2839 | 2903 | 2967 | 3031 | 3094 | 3158 | 3222 | 3285
| 8.5 | 2536 | 2607 | 2679 | 2750 | 2821 | 2893 | 2964 | 3036 | 3107 | 3178 | 3249 | 3321 | 3392 | 3463 | 3534 | 3605 | 3676
| 9 | 2793 | 2872 | 2950 | 3029 | 3107 | 3186 | 3264 | 3342 | 3420 | 3499 | 3577 | 3655 | 3733 | 3811 | 3890 | 3968 | 4045
| 9.5 | 3041 | 3126 | 3212 | 3297 | 3382 | 3467 | 3552 | 3637 | 3722 | 3807 | 3892 | 3977 | 4063 | 4146 | 4228 | 4310 | 4379
| 10 | 3275 | 3367 | 3459 | 3550 | 3642 | 3733 | 3825 | 3916 | 4007 | 4099 | 4191 | 4279 | 4365 | 4441 | 4508 | 4575 | 4629
| 10.5 | 3497 | 3594 | 3692 | 3790 | 3887 | 3985 | 4082 | 4180 | 4278 | 4369 | 4459 | 4534 | 4604 | 4665 | 4718 | 4770 | 4811
| 11 | 3709 | 3813 | 3916 | 4019 | 4122 | 4226 | 4331 | 4424 | 4519 | 4594 | 4667 | 4726 | 4782 | 4829 | 4867 | 4906 | 4933
| 11.5 | 3917 | 4026 | 4135 | 4244 | 4354 | 4452 | 4547 | 4624 | 4702 | 4762 | 4820 | 4865 | 4906 | 4940 | 4965 | 4990 | 5004
| 12 | 4121 | 4236 | 4351 | 4454 | 4553 | 4634 | 4712 | 4775 | 4837 | 4882 | 4926 | 4957 | 4985 | 5004 | 5015 | 5027 | 5030
| 12.5 | 4322 | 4436 | 4537 | 4625 | 4707 | 4772 | 4834 | 4883 | 4930 | 4961 | 4991 | 5008 | 5022 | 5029 | 5030 | 5030 | 5030
| 13 | 4504 | 4602 | 4687 | 4758 | 4825 | 4875 | 4923 | 4957 | 4990 | 5007 | 5023 | 5028 | 5030 | 5030 | 5030 | 5030 | 5030
| 13.5 | 4654 | 4737 | 4806 | 4862 | 4914 | 4950 | 4983 | 5004 | 5023 | 5027 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030
| 14 | 4777 | 4844 | 4899 | 4940 | 4977 | 4999 | 5019 | 5025 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030
| 14.5 | 4873 | 4925 | 4966 | 4993 | 5016 | 5025 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030
| 15 | 4944 | 4982 | 5009 | 5022 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030
| 15.5 | 4992 | 5016 | 5028 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030
| 16 | 5019 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030
| 16.5 | 5029 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030
| 17 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030
| 17.5 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030
| 18 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030
| 18.5 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030
| 19 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030
| 19.5 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030
| 20 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030 | 5030

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874
| 3.5 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867
| 4 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852
| 4.5 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839
| 5 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83
| 5.5 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824 | 0.824
| 6 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81
| 6.5 | 0.776 | 0.776 | 0.776 | 0.776 | 0.776 | 0.776 | 0.776 | 0.776 | 0.776 | 0.776 | 0.776 | 0.776 | 0.776 | 0.776 | 0.776 | 0.776 | 0.776
| 7 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734 | 0.734
| 7.5 | 0.685 | 0.685 | 0.685 | 0.685 | 0.685 | 0.685 | 0.685 | 0.685 | 0.685 | 0.685 | 0.685 | 0.685 | 0.685 | 0.685 | 0.685 | 0.685 | 0.685
| 8 | 0.634 | 0.634 | 0.634 | 0.634 | 0.634 | 0.634 | 0.634 | 0.634 | 0.634 | 0.634 | 0.634 | 0.634 | 0.634 | 0.634 | 0.634 | 0.634 | 0.634
| 8.5 | 0.583 | 0.583 | 0.583 | 0.583 | 0.583 | 0.583 | 0.583 | 0.583 | 0.583 | 0.583 | 0.583 | 0.583 | 0.583 | 0.583 | 0.583 | 0.582 | 0.581
| 9 | 0.531 | 0.531 | 0.531 | 0.531 | 0.531 | 0.531 | 0.531 | 0.531 | 0.531 | 0.531 | 0.531 | 0.531 | 0.53 | 0.529 | 0.528 | 0.527 | 0.525
| 9.5 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.479 | 0.48 | 0.48 | 0.479 | 0.479 | 0.478 | 0.478 | 0.476 | 0.475 | 0.473 | 0.471 | 0.469
| 10 | 0.433 | 0.433 | 0.433 | 0.433 | 0.433 | 0.433 | 0.433 | 0.432 | 0.432 | 0.431 | 0.429 | 0.428 | 0.426 | 0.424 | 0.422 | 0.419 | 0.417
| 10.5 | 0.393 | 0.393 | 0.393 | 0.393 | 0.393 | 0.392 | 0.392 | 0.39 | 0.389 | 0.388 | 0.386 | 0.384 | 0.382 | 0.379 | 0.377 | 0.374 | 0.371
| 11 | 0.359 | 0.359 | 0.358 | 0.358 | 0.357 | 0.356 | 0.354 | 0.353 | 0.351 | 0.349 | 0.347 | 0.345 | 0.342 | 0.339 | 0.337 | 0.334 | 0.33
| 11.5 | 0.328 | 0.327 | 0.327 | 0.325 | 0.324 | 0.323 | 0.321 | 0.319 | 0.317 | 0.315 | 0.312 | 0.31 | 0.307 | 0.304 | 0.301 | 0.298 | 0.295
| 12 | 0.3 | 0.299 | 0.298 | 0.296 | 0.295 | 0.293 | 0.291 | 0.289 | 0.286 | 0.284 | 0.281 | 0.279 | 0.276 | 0.273 | 0.27 | 0.266 | 0.263
| 12.5 | 0.275 | 0.274 | 0.272 | 0.27 | 0.268 | 0.266 | 0.264 | 0.262 | 0.259 | 0.257 | 0.254 | 0.251 | 0.248 | 0.245 | 0.242 | 0.238 | 0.235
| 13 | 0.252 | 0.251 | 0.249 | 0.247 | 0.245 | 0.242 | 0.24 | 0.237 | 0.235 | 0.232 | 0.229 | 0.226 | 0.223 | 0.22 | 0.217 | 0.213 | 0.21
| 13.5 | 0.232 | 0.23 | 0.228 | 0.226 | 0.223 | 0.221 | 0.218 | 0.216 | 0.213 | 0.21 | 0.207 | 0.204 | 0.201 | 0.198 | 0.194 | 0.191 | 0.188
| 14 | 0.213 | 0.211 | 0.209 | 0.206 | 0.204 | 0.201 | 0.198 | 0.196 | 0.193 | 0.19 | 0.187 | 0.184 | 0.181 | 0.178 | 0.174 | 0.171 | 0.168
| 14.5 | 0.196 | 0.193 | 0.191 | 0.189 | 0.186 | 0.183 | 0.181 | 0.178 | 0.175 | 0.172 | 0.169 | 0.166 | 0.163 | 0.16 | 0.156 | 0.153 | 0.15
| 15 | 0.18 | 0.178 | 0.175 | 0.173 | 0.17 | 0.167 | 0.165 | 0.162 | 0.159 | 0.156 | 0.153 | 0.15 | 0.147 | 0.144 | 0.141 | 0.138 | 0.136
| 15.5 | 0.166 | 0.163 | 0.161 | 0.158 | 0.156 | 0.153 | 0.15 | 0.147 | 0.144 | 0.141 | 0.138 | 0.135 | 0.133 | 0.13 | 0.128 | 0.125 | 0.123
| 16 | 0.153 | 0.15 | 0.148 | 0.145 | 0.143 | 0.14 | 0.137 | 0.134 | 0.131 | 0.128 | 0.126 | 0.123 | 0.121 | 0.118 | 0.116 | 0.114 | 0.112
| 16.5 | 0.142 | 0.139 | 0.136 | 0.134 | 0.131 | 0.128 | 0.125 | 0.123 | 0.12 | 0.117 | 0.115 | 0.112 | 0.11 | 0.108 | 0.106 | 0.104 | 0.102
| 17 | 0.132 | 0.129 | 0.126 | 0.124 | 0.121 | 0.118 | 0.115 | 0.113 | 0.11 | 0.108 | 0.106 | 0.104 | 0.101 | 0.1 | 0.098 | 0.096 | 0.094
| 17.5 | 0.123 | 0.12 | 0.117 | 0.115 | 0.112 | 0.109 | 0.107 | 0.104 | 0.102 | 0.1 | 0.098 | 0.096 | 0.094 | 0.092 | 0.091 | 0.089 | 0.087
| 18 | 0.115 | 0.112 | 0.109 | 0.107 | 0.104 | 0.102 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.088 | 0.086 | 0.084 | 0.083 | 0.082
| 18.5 | 0.108 | 0.105 | 0.103 | 0.1 | 0.098 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084 | 0.082 | 0.081 | 0.079 | 0.078 | 0.077
| 19 | 0.1 | 0.097 | 0.095 | 0.092 | 0.09 | 0.088 | 0.086 | 0.084 | 0.082 | 0.08 | 0.079 | 0.077 | 0.076 | 0.075 | 0.073 | 0.072 | 0.071
| 19.5 | 0.091 | 0.088 | 0.086 | 0.084 | 0.082 | 0.08 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.07 | 0.069 | 0.068 | 0.066 | 0.065 | 0.065
| 20 | 0.082 | 0.079 | 0.078 | 0.076 | 0.074 | 0.072 | 0.07 | 0.069 | 0.067 | 0.066 | 0.065 | 0.064 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058