## Sheet1
PROPERTIES
General
Name | N175-6.X MW 50-60 Hz vM8_4820_h112
Manufacturer | Nordex
Hub Height | 112
Power
Rated Power | 4820
Peak Power | 4820
Power Regulation Type | Pitch
Voltage | 950
Rotor
Rotor diameter | 175
Number of blades | 3
Rated RPM | -
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 20
Restart Wind Speed | 19.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -40
Low Temperature Restart | -20
High Temperature Shutdown | 40
High Temperature Restart | 45
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 38.5
Design TI | 0.35

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 48 | 50 | 53 | 56 | 59 | 61 | 64 | 67 | 69 | 72 | 75 | 78 | 80
| 3.5 | 146 | 151 | 156 | 162 | 167 | 172 | 177 | 182 | 187 | 193 | 198 | 203 | 208
| 4 | 279 | 288 | 296 | 305 | 313 | 322 | 330 | 339 | 347 | 356 | 364 | 373 | 381
| 4.5 | 447 | 459 | 472 | 485 | 497 | 510 | 523 | 535 | 548 | 561 | 573 | 586 | 599
| 5 | 647 | 665 | 683 | 700 | 718 | 736 | 753 | 771 | 789 | 806 | 824 | 842 | 859
| 5.5 | 886 | 910 | 933 | 957 | 980 | 1004 | 1028 | 1051 | 1075 | 1098 | 1122 | 1146 | 1169
| 6 | 1169 | 1199 | 1230 | 1260 | 1291 | 1322 | 1352 | 1383 | 1413 | 1444 | 1475 | 1505 | 1536
| 6.5 | 1492 | 1530 | 1569 | 1608 | 1646 | 1685 | 1723 | 1762 | 1801 | 1839 | 1878 | 1916 | 1955
| 7 | 1827 | 1874 | 1921 | 1968 | 2015 | 2062 | 2109 | 2156 | 2202 | 2249 | 2296 | 2343 | 2390
| 7.5 | 2155 | 2210 | 2265 | 2320 | 2375 | 2430 | 2485 | 2540 | 2595 | 2650 | 2704 | 2759 | 2814
| 8 | 2461 | 2523 | 2586 | 2648 | 2711 | 2773 | 2836 | 2898 | 2961 | 3023 | 3085 | 3148 | 3210
| 8.5 | 2744 | 2813 | 2883 | 2952 | 3021 | 3091 | 3160 | 3229 | 3299 | 3368 | 3437 | 3506 | 3576
| 9 | 3013 | 3089 | 3166 | 3242 | 3318 | 3394 | 3469 | 3545 | 3621 | 3697 | 3773 | 3849 | 3924
| 9.5 | 3273 | 3355 | 3438 | 3520 | 3602 | 3685 | 3767 | 3850 | 3932 | 4013 | 4093 | 4171 | 4232
| 10 | 3515 | 3604 | 3692 | 3780 | 3868 | 3957 | 4046 | 4130 | 4213 | 4286 | 4351 | 4415 | 4462
| 10.5 | 3748 | 3841 | 3935 | 4030 | 4125 | 4212 | 4298 | 4367 | 4434 | 4493 | 4544 | 4594 | 4629
| 11 | 3969 | 4070 | 4170 | 4260 | 4349 | 4420 | 4489 | 4546 | 4598 | 4643 | 4680 | 4717 | 4739
| 11.5 | 4188 | 4280 | 4373 | 4446 | 4519 | 4575 | 4631 | 4673 | 4711 | 4743 | 4768 | 4791 | 4800
| 12 | 4373 | 4450 | 4526 | 4584 | 4643 | 4685 | 4726 | 4756 | 4780 | 4799 | 4810 | 4820 | 4820
| 12.5 | 4517 | 4578 | 4640 | 4684 | 4728 | 4757 | 4785 | 4801 | 4812 | 4819 | 4820 | 4820 | 4820
| 13 | 4630 | 4677 | 4724 | 4754 | 4785 | 4801 | 4815 | 4819 | 4819 | 4820 | 4820 | 4820 | 4820
| 13.5 | 4713 | 4746 | 4780 | 4797 | 4815 | 4818 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820
| 14 | 4772 | 4792 | 4812 | 4817 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820
| 14.5 | 4808 | 4814 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820
| 15 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820
| 15.5 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820
| 16 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820
| 16.5 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820
| 17 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820
| 17.5 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820
| 18 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820
| 18.5 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820
| 19 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820
| 19.5 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820
| 20 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874
| 3.5 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867
| 4 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852
| 4.5 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839
| 5 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83
| 5.5 | 0.822 | 0.822 | 0.822 | 0.822 | 0.822 | 0.822 | 0.822 | 0.822 | 0.822 | 0.822 | 0.822 | 0.822 | 0.822
| 6 | 0.801 | 0.801 | 0.801 | 0.801 | 0.801 | 0.801 | 0.801 | 0.801 | 0.801 | 0.801 | 0.801 | 0.801 | 0.801
| 6.5 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764
| 7 | 0.718 | 0.718 | 0.718 | 0.718 | 0.718 | 0.718 | 0.718 | 0.718 | 0.718 | 0.718 | 0.718 | 0.718 | 0.718
| 7.5 | 0.668 | 0.668 | 0.668 | 0.668 | 0.668 | 0.668 | 0.668 | 0.668 | 0.668 | 0.668 | 0.668 | 0.668 | 0.668
| 8 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615
| 8.5 | 0.562 | 0.562 | 0.562 | 0.562 | 0.562 | 0.562 | 0.562 | 0.562 | 0.562 | 0.562 | 0.562 | 0.562 | 0.561
| 9 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.509 | 0.508 | 0.507 | 0.506 | 0.504
| 9.5 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.459 | 0.459 | 0.458 | 0.456 | 0.455 | 0.453 | 0.451 | 0.449
| 10 | 0.415 | 0.415 | 0.415 | 0.414 | 0.414 | 0.413 | 0.411 | 0.41 | 0.408 | 0.406 | 0.404 | 0.402 | 0.399
| 10.5 | 0.377 | 0.376 | 0.375 | 0.374 | 0.373 | 0.371 | 0.369 | 0.367 | 0.365 | 0.363 | 0.361 | 0.358 | 0.355
| 11 | 0.342 | 0.341 | 0.339 | 0.338 | 0.336 | 0.334 | 0.332 | 0.33 | 0.327 | 0.325 | 0.322 | 0.319 | 0.316
| 11.5 | 0.31 | 0.309 | 0.307 | 0.305 | 0.303 | 0.301 | 0.299 | 0.296 | 0.294 | 0.291 | 0.288 | 0.285 | 0.282
| 12 | 0.282 | 0.281 | 0.279 | 0.276 | 0.274 | 0.272 | 0.269 | 0.267 | 0.264 | 0.261 | 0.258 | 0.255 | 0.252
| 12.5 | 0.257 | 0.255 | 0.253 | 0.251 | 0.248 | 0.246 | 0.243 | 0.24 | 0.237 | 0.234 | 0.231 | 0.228 | 0.225
| 13 | 0.234 | 0.232 | 0.23 | 0.227 | 0.225 | 0.222 | 0.219 | 0.216 | 0.213 | 0.21 | 0.207 | 0.204 | 0.201
| 13.5 | 0.214 | 0.211 | 0.209 | 0.206 | 0.204 | 0.201 | 0.198 | 0.195 | 0.192 | 0.189 | 0.186 | 0.183 | 0.179
| 14 | 0.195 | 0.192 | 0.19 | 0.187 | 0.185 | 0.182 | 0.179 | 0.176 | 0.173 | 0.17 | 0.167 | 0.163 | 0.16
| 14.5 | 0.178 | 0.175 | 0.173 | 0.17 | 0.167 | 0.165 | 0.162 | 0.159 | 0.156 | 0.152 | 0.149 | 0.147 | 0.144
| 15 | 0.163 | 0.16 | 0.157 | 0.155 | 0.152 | 0.149 | 0.146 | 0.143 | 0.14 | 0.137 | 0.135 | 0.132 | 0.13
| 15.5 | 0.149 | 0.146 | 0.144 | 0.141 | 0.138 | 0.135 | 0.132 | 0.13 | 0.127 | 0.124 | 0.122 | 0.12 | 0.118
| 16 | 0.136 | 0.134 | 0.131 | 0.128 | 0.126 | 0.123 | 0.12 | 0.118 | 0.115 | 0.113 | 0.111 | 0.109 | 0.107
| 16.5 | 0.125 | 0.123 | 0.12 | 0.117 | 0.115 | 0.112 | 0.11 | 0.108 | 0.106 | 0.104 | 0.102 | 0.1 | 0.098
| 17 | 0.116 | 0.113 | 0.11 | 0.108 | 0.106 | 0.103 | 0.101 | 0.099 | 0.097 | 0.095 | 0.094 | 0.092 | 0.09
| 17.5 | 0.107 | 0.105 | 0.102 | 0.1 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.087 | 0.085 | 0.084
| 18 | 0.1 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084 | 0.083 | 0.081 | 0.08 | 0.078
| 18.5 | 0.093 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084 | 0.082 | 0.08 | 0.079 | 0.077 | 0.076 | 0.075 | 0.073
| 19 | 0.086 | 0.084 | 0.082 | 0.08 | 0.079 | 0.077 | 0.076 | 0.074 | 0.073 | 0.071 | 0.07 | 0.069 | 0.067
| 19.5 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.07 | 0.069 | 0.067 | 0.066 | 0.065 | 0.064 | 0.063 | 0.061
| 20 | 0.07 | 0.069 | 0.067 | 0.066 | 0.065 | 0.064 | 0.062 | 0.06 | 0.06 | 0.058 | 0.057 | 0.057 | 0.055