## Sheet1
PROPERTIES
General
Name | N175-6.X MW 50-60 Hz vM8_4820
Manufacturer | Nordex
Hub Height | 142 | 179
Power
Rated Power | 4820
Peak Power | 4820
Power Regulation Type | Pitch
Voltage | 950
Rotor
Rotor diameter | 175
Number of blades | 3
Rated RPM | -
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 20
Restart Wind Speed | 19.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -40
Low Temperature Restart | -20
High Temperature Shutdown | 40
High Temperature Restart | 45
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 39.6
Design TI | 0.35

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 49 | 52 | 54 | 57 | 60 | 63 | 65 | 68 | 71 | 74 | 76 | 79 | 82
| 3.5 | 148 | 154 | 159 | 164 | 169 | 174 | 180 | 185 | 190 | 195 | 201 | 206 | 211
| 4 | 283 | 292 | 300 | 309 | 317 | 326 | 335 | 343 | 352 | 360 | 369 | 378 | 386
| 4.5 | 452 | 465 | 477 | 490 | 503 | 516 | 529 | 541 | 554 | 567 | 580 | 593 | 605
| 5 | 655 | 673 | 690 | 708 | 726 | 744 | 762 | 780 | 797 | 815 | 833 | 851 | 869
| 5.5 | 896 | 919 | 943 | 967 | 991 | 1015 | 1039 | 1062 | 1086 | 1110 | 1134 | 1158 | 1181
| 6 | 1181 | 1212 | 1243 | 1273 | 1304 | 1335 | 1366 | 1397 | 1428 | 1459 | 1489 | 1520 | 1551
| 6.5 | 1507 | 1546 | 1585 | 1624 | 1663 | 1702 | 1741 | 1779 | 1818 | 1857 | 1896 | 1935 | 1974
| 7 | 1845 | 1893 | 1940 | 1987 | 2035 | 2082 | 2129 | 2176 | 2223 | 2271 | 2318 | 2365 | 2412
| 7.5 | 2176 | 2231 | 2287 | 2342 | 2397 | 2453 | 2508 | 2563 | 2619 | 2674 | 2729 | 2784 | 2840
| 8 | 2484 | 2547 | 2610 | 2673 | 2736 | 2799 | 2862 | 2924 | 2987 | 3050 | 3113 | 3176 | 3238
| 8.5 | 2769 | 2839 | 2909 | 2979 | 3049 | 3118 | 3188 | 3258 | 3328 | 3397 | 3467 | 3537 | 3606
| 9 | 3040 | 3117 | 3194 | 3270 | 3347 | 3423 | 3500 | 3576 | 3652 | 3729 | 3805 | 3881 | 3956
| 9.5 | 3302 | 3385 | 3468 | 3551 | 3633 | 3716 | 3799 | 3882 | 3965 | 4045 | 4125 | 4197 | 4258
| 10 | 3546 | 3635 | 3724 | 3812 | 3901 | 3991 | 4078 | 4162 | 4247 | 4313 | 4378 | 4435 | 4483
| 10.5 | 3779 | 3874 | 3969 | 4064 | 4157 | 4245 | 4324 | 4392 | 4463 | 4514 | 4565 | 4609 | 4643
| 11 | 4003 | 4104 | 4200 | 4291 | 4376 | 4447 | 4510 | 4564 | 4620 | 4658 | 4696 | 4726 | 4748
| 11.5 | 4219 | 4312 | 4397 | 4472 | 4541 | 4597 | 4646 | 4686 | 4728 | 4753 | 4778 | 4795 | 4803
| 12 | 4399 | 4476 | 4545 | 4605 | 4659 | 4701 | 4736 | 4763 | 4792 | 4804 | 4815 | 4820 | 4820
| 12.5 | 4538 | 4599 | 4654 | 4700 | 4740 | 4768 | 4790 | 4803 | 4819 | 4820 | 4820 | 4820 | 4820
| 13 | 4646 | 4693 | 4733 | 4765 | 4792 | 4807 | 4816 | 4818 | 4820 | 4820 | 4820 | 4820 | 4820
| 13.5 | 4724 | 4758 | 4785 | 4803 | 4817 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820
| 14 | 4777 | 4799 | 4813 | 4818 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820
| 14.5 | 4809 | 4817 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820
| 15 | 4819 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820
| 15.5 | 4819 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820
| 16 | 4819 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820
| 16.5 | 4819 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820
| 17 | 4819 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820
| 17.5 | 4819 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820
| 18 | 4819 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820
| 18.5 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820
| 19 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820
| 19.5 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820
| 20 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820 | 4820

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
TI (%) | 10 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874
| 3.5 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867
| 4 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852
| 4.5 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839
| 5 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83
| 5.5 | 0.822 | 0.822 | 0.822 | 0.822 | 0.822 | 0.822 | 0.822 | 0.822 | 0.822 | 0.822 | 0.822 | 0.822 | 0.822
| 6 | 0.801 | 0.801 | 0.801 | 0.801 | 0.801 | 0.801 | 0.801 | 0.801 | 0.801 | 0.801 | 0.801 | 0.801 | 0.801
| 6.5 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764 | 0.764
| 7 | 0.718 | 0.718 | 0.718 | 0.718 | 0.718 | 0.718 | 0.718 | 0.718 | 0.718 | 0.718 | 0.718 | 0.718 | 0.718
| 7.5 | 0.668 | 0.668 | 0.668 | 0.668 | 0.668 | 0.668 | 0.668 | 0.668 | 0.668 | 0.668 | 0.668 | 0.668 | 0.668
| 8 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615
| 8.5 | 0.562 | 0.562 | 0.562 | 0.562 | 0.562 | 0.562 | 0.562 | 0.562 | 0.562 | 0.562 | 0.562 | 0.562 | 0.561
| 9 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.509 | 0.509 | 0.508 | 0.507 | 0.505
| 9.5 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.459 | 0.459 | 0.458 | 0.457 | 0.455 | 0.454 | 0.452 | 0.45
| 10 | 0.415 | 0.415 | 0.415 | 0.415 | 0.414 | 0.413 | 0.412 | 0.41 | 0.409 | 0.407 | 0.405 | 0.403 | 0.4
| 10.5 | 0.377 | 0.376 | 0.375 | 0.374 | 0.373 | 0.372 | 0.37 | 0.368 | 0.366 | 0.364 | 0.362 | 0.359 | 0.356
| 11 | 0.342 | 0.341 | 0.34 | 0.338 | 0.337 | 0.335 | 0.333 | 0.331 | 0.329 | 0.326 | 0.323 | 0.321 | 0.317
| 11.5 | 0.311 | 0.309 | 0.308 | 0.306 | 0.304 | 0.302 | 0.3 | 0.297 | 0.295 | 0.292 | 0.289 | 0.286 | 0.283
| 12 | 0.283 | 0.281 | 0.279 | 0.277 | 0.275 | 0.273 | 0.27 | 0.267 | 0.265 | 0.262 | 0.259 | 0.256 | 0.253
| 12.5 | 0.258 | 0.256 | 0.254 | 0.251 | 0.249 | 0.246 | 0.244 | 0.241 | 0.238 | 0.235 | 0.232 | 0.229 | 0.226
| 13 | 0.235 | 0.233 | 0.23 | 0.228 | 0.226 | 0.223 | 0.22 | 0.217 | 0.215 | 0.212 | 0.209 | 0.205 | 0.202
| 13.5 | 0.214 | 0.212 | 0.21 | 0.207 | 0.205 | 0.202 | 0.199 | 0.196 | 0.193 | 0.19 | 0.187 | 0.184 | 0.181
| 14 | 0.196 | 0.193 | 0.191 | 0.188 | 0.186 | 0.183 | 0.18 | 0.177 | 0.174 | 0.171 | 0.168 | 0.165 | 0.162
| 14.5 | 0.179 | 0.176 | 0.174 | 0.171 | 0.168 | 0.166 | 0.163 | 0.16 | 0.157 | 0.154 | 0.151 | 0.148 | 0.145
| 15 | 0.163 | 0.161 | 0.158 | 0.156 | 0.153 | 0.15 | 0.147 | 0.144 | 0.141 | 0.139 | 0.136 | 0.133 | 0.131
| 15.5 | 0.15 | 0.147 | 0.145 | 0.142 | 0.139 | 0.136 | 0.133 | 0.131 | 0.128 | 0.125 | 0.123 | 0.121 | 0.118
| 16 | 0.137 | 0.135 | 0.132 | 0.129 | 0.127 | 0.124 | 0.121 | 0.119 | 0.116 | 0.114 | 0.112 | 0.11 | 0.108
| 16.5 | 0.126 | 0.124 | 0.121 | 0.118 | 0.116 | 0.113 | 0.111 | 0.109 | 0.106 | 0.104 | 0.102 | 0.1 | 0.099
| 17 | 0.117 | 0.114 | 0.111 | 0.109 | 0.106 | 0.104 | 0.102 | 0.1 | 0.098 | 0.096 | 0.094 | 0.093 | 0.091
| 17.5 | 0.108 | 0.105 | 0.103 | 0.101 | 0.099 | 0.096 | 0.094 | 0.093 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084
| 18 | 0.101 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083 | 0.082 | 0.08 | 0.079
| 18.5 | 0.094 | 0.092 | 0.09 | 0.088 | 0.086 | 0.084 | 0.083 | 0.081 | 0.079 | 0.078 | 0.077 | 0.075 | 0.074
| 19 | 0.087 | 0.085 | 0.083 | 0.081 | 0.079 | 0.077 | 0.077 | 0.075 | 0.073 | 0.072 | 0.071 | 0.069 | 0.068
| 19.5 | 0.079 | 0.077 | 0.076 | 0.074 | 0.072 | 0.07 | 0.07 | 0.068 | 0.066 | 0.065 | 0.065 | 0.063 | 0.062
| 20 | 0.071 | 0.07 | 0.068 | 0.067 | 0.065 | 0.064 | 0.063 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056