## Sheet1
PROPERTIES
General
Name | N175-6.X MW 50-60 Hz vM9_4520
Manufacturer | Nordex
Hub Height | 142 | 179
Power
Rated Power | 4520
Peak Power | 4520
Power Regulation Type | Pitch
Voltage | 950
Rotor
Rotor diameter | 175
Number of blades | 3
Rated RPM | -
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 20
Restart Wind Speed | 19.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -40
Low Temperature Restart | -20
High Temperature Shutdown | 40
High Temperature Restart | 45
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | -
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 39.6
Design TI | 0.35

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 49 | 52 | 54 | 57 | 60 | 63 | 65 | 68 | 71 | 74 | 76 | 79 | 82
| 3.5 | 148 | 154 | 159 | 164 | 169 | 174 | 180 | 185 | 190 | 195 | 201 | 206 | 211
| 4 | 283 | 292 | 300 | 309 | 317 | 326 | 335 | 343 | 352 | 360 | 369 | 378 | 386
| 4.5 | 452 | 465 | 477 | 490 | 503 | 516 | 529 | 541 | 554 | 567 | 580 | 593 | 605
| 5 | 655 | 673 | 690 | 708 | 726 | 744 | 762 | 780 | 797 | 815 | 833 | 851 | 869
| 5.5 | 896 | 920 | 943 | 967 | 991 | 1015 | 1039 | 1062 | 1086 | 1110 | 1134 | 1158 | 1181
| 6 | 1180 | 1211 | 1242 | 1273 | 1304 | 1335 | 1365 | 1396 | 1427 | 1458 | 1489 | 1520 | 1550
| 6.5 | 1499 | 1538 | 1576 | 1615 | 1654 | 1693 | 1731 | 1770 | 1809 | 1847 | 1886 | 1925 | 1963
| 7 | 1823 | 1869 | 1916 | 1963 | 2010 | 2056 | 2103 | 2150 | 2196 | 2243 | 2289 | 2336 | 2383
| 7.5 | 2134 | 2188 | 2242 | 2297 | 2351 | 2406 | 2460 | 2514 | 2568 | 2623 | 2677 | 2731 | 2785
| 8 | 2421 | 2482 | 2544 | 2605 | 2666 | 2728 | 2789 | 2850 | 2912 | 2973 | 3034 | 3095 | 3157
| 8.5 | 2689 | 2757 | 2825 | 2893 | 2960 | 3028 | 3096 | 3164 | 3232 | 3300 | 3367 | 3435 | 3503
| 9 | 2946 | 3021 | 3095 | 3169 | 3243 | 3318 | 3392 | 3466 | 3540 | 3614 | 3688 | 3760 | 3833
| 9.5 | 3190 | 3270 | 3350 | 3431 | 3511 | 3591 | 3671 | 3751 | 3829 | 3906 | 3973 | 4032 | 4092
| 10 | 3420 | 3506 | 3591 | 3677 | 3764 | 3848 | 3929 | 4008 | 4071 | 4134 | 4187 | 4234 | 4280
| 10.5 | 3639 | 3731 | 3823 | 3912 | 3996 | 4073 | 4140 | 4204 | 4253 | 4303 | 4342 | 4376 | 4409
| 11 | 3853 | 3945 | 4032 | 4112 | 4180 | 4242 | 4295 | 4345 | 4382 | 4418 | 4445 | 4467 | 4488
| 11.5 | 4047 | 4125 | 4197 | 4261 | 4315 | 4364 | 4403 | 4440 | 4464 | 4487 | 4502 | 4510 | 4518
| 12 | 4198 | 4262 | 4319 | 4370 | 4409 | 4444 | 4471 | 4495 | 4506 | 4516 | 4520 | 4520 | 4520
| 12.5 | 4315 | 4364 | 4407 | 4445 | 4472 | 4494 | 4508 | 4519 | 4520 | 4520 | 4520 | 4520 | 4520
| 13 | 4402 | 4438 | 4469 | 4493 | 4507 | 4517 | 4519 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 13.5 | 4464 | 4487 | 4505 | 4517 | 4518 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 14 | 4503 | 4514 | 4518 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 14.5 | 4519 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 15 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 15.5 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 16 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 16.5 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 17 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 17.5 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 18 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 18.5 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 19 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 19.5 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520
| 20 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520 | 4520

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
TI (%) | 10 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874 | 0.874
| 3.5 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867 | 0.867
| 4 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852 | 0.852
| 4.5 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839 | 0.839
| 5 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83
| 5.5 | 0.821 | 0.821 | 0.821 | 0.821 | 0.821 | 0.821 | 0.821 | 0.821 | 0.821 | 0.821 | 0.821 | 0.821 | 0.821
| 6 | 0.794 | 0.794 | 0.794 | 0.794 | 0.794 | 0.794 | 0.794 | 0.794 | 0.794 | 0.794 | 0.794 | 0.794 | 0.794
| 6.5 | 0.752 | 0.752 | 0.752 | 0.752 | 0.752 | 0.752 | 0.752 | 0.752 | 0.752 | 0.752 | 0.752 | 0.752 | 0.752
| 7 | 0.703 | 0.703 | 0.703 | 0.703 | 0.703 | 0.703 | 0.703 | 0.703 | 0.703 | 0.703 | 0.703 | 0.703 | 0.703
| 7.5 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651
| 8 | 0.597 | 0.597 | 0.597 | 0.597 | 0.597 | 0.597 | 0.597 | 0.597 | 0.597 | 0.597 | 0.597 | 0.597 | 0.597
| 8.5 | 0.543 | 0.543 | 0.543 | 0.543 | 0.543 | 0.543 | 0.543 | 0.543 | 0.543 | 0.543 | 0.542 | 0.541 | 0.541
| 9 | 0.489 | 0.489 | 0.489 | 0.489 | 0.489 | 0.489 | 0.489 | 0.489 | 0.488 | 0.487 | 0.486 | 0.484 | 0.483
| 9.5 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.439 | 0.439 | 0.438 | 0.436 | 0.435 | 0.433 | 0.431 | 0.429
| 10 | 0.398 | 0.398 | 0.397 | 0.397 | 0.396 | 0.394 | 0.393 | 0.392 | 0.389 | 0.388 | 0.385 | 0.383 | 0.38
| 10.5 | 0.361 | 0.36 | 0.359 | 0.358 | 0.356 | 0.354 | 0.353 | 0.351 | 0.348 | 0.346 | 0.343 | 0.341 | 0.338
| 11 | 0.327 | 0.325 | 0.324 | 0.322 | 0.321 | 0.319 | 0.316 | 0.314 | 0.312 | 0.309 | 0.306 | 0.303 | 0.301
| 11.5 | 0.297 | 0.295 | 0.293 | 0.291 | 0.289 | 0.287 | 0.284 | 0.282 | 0.279 | 0.277 | 0.274 | 0.271 | 0.268
| 12 | 0.269 | 0.267 | 0.265 | 0.263 | 0.261 | 0.259 | 0.256 | 0.253 | 0.251 | 0.248 | 0.245 | 0.242 | 0.239
| 12.5 | 0.245 | 0.243 | 0.241 | 0.238 | 0.236 | 0.233 | 0.231 | 0.228 | 0.225 | 0.222 | 0.219 | 0.216 | 0.213
| 13 | 0.223 | 0.221 | 0.218 | 0.216 | 0.213 | 0.211 | 0.208 | 0.205 | 0.202 | 0.199 | 0.196 | 0.193 | 0.19
| 13.5 | 0.203 | 0.201 | 0.198 | 0.196 | 0.193 | 0.19 | 0.188 | 0.185 | 0.182 | 0.179 | 0.176 | 0.172 | 0.169
| 14 | 0.185 | 0.183 | 0.18 | 0.178 | 0.175 | 0.172 | 0.169 | 0.166 | 0.163 | 0.16 | 0.157 | 0.154 | 0.151
| 14.5 | 0.169 | 0.166 | 0.164 | 0.161 | 0.158 | 0.156 | 0.153 | 0.15 | 0.147 | 0.144 | 0.141 | 0.138 | 0.136
| 15 | 0.154 | 0.152 | 0.149 | 0.146 | 0.144 | 0.141 | 0.138 | 0.135 | 0.132 | 0.13 | 0.127 | 0.125 | 0.122
| 15.5 | 0.141 | 0.139 | 0.136 | 0.133 | 0.13 | 0.128 | 0.125 | 0.122 | 0.12 | 0.118 | 0.115 | 0.113 | 0.111
| 16 | 0.129 | 0.127 | 0.124 | 0.121 | 0.119 | 0.116 | 0.114 | 0.111 | 0.109 | 0.107 | 0.105 | 0.103 | 0.101
| 16.5 | 0.119 | 0.116 | 0.113 | 0.111 | 0.108 | 0.106 | 0.104 | 0.102 | 0.1 | 0.098 | 0.096 | 0.094 | 0.093
| 17 | 0.109 | 0.107 | 0.104 | 0.102 | 0.1 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.089 | 0.087 | 0.085
| 17.5 | 0.101 | 0.099 | 0.097 | 0.095 | 0.092 | 0.091 | 0.089 | 0.087 | 0.085 | 0.084 | 0.082 | 0.081 | 0.079
| 18 | 0.094 | 0.092 | 0.09 | 0.088 | 0.086 | 0.084 | 0.083 | 0.081 | 0.08 | 0.078 | 0.077 | 0.075 | 0.074
| 18.5 | 0.088 | 0.086 | 0.085 | 0.083 | 0.081 | 0.079 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.071 | 0.07
| 19 | 0.081 | 0.079 | 0.078 | 0.077 | 0.075 | 0.073 | 0.072 | 0.07 | 0.069 | 0.067 | 0.066 | 0.065 | 0.065
| 19.5 | 0.074 | 0.072 | 0.071 | 0.07 | 0.068 | 0.066 | 0.065 | 0.064 | 0.063 | 0.061 | 0.06 | 0.06 | 0.059
| 20 | 0.067 | 0.065 | 0.064 | 0.063 | 0.061 | 0.06 | 0.059 | 0.057 | 0.057 | 0.055 | 0.054 | 0.054 | 0.053