## Sheet1
PROPERTIES
General
Name | Nordex N131/3.9 Mode 0 3,9MW
Manufacturer | Nordex
Hub Height | 84 | 114 | 120 | 134 | 164
Power
Rated Power | 3900
Peak Power | 3900
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 131
Number of blades | 3
Rated RPM | 12.6
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 25
Restart Wind Speed | 19.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 40
High Temperature Restart | 38
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | III
Turbine SubClass | S
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 40
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 1 | 3 | 4 | 5 | 7 | 8 | 9 | 10 | 12 | 13 | 14 | 15 | 17 | 18 | 19 | 21 | 22
| 3.5 | 52 | 55 | 58 | 61 | 63 | 66 | 69 | 71 | 74 | 77 | 79 | 82 | 85 | 87 | 90 | 93 | 95
| 4 | 122 | 127 | 132 | 136 | 141 | 146 | 150 | 155 | 159 | 164 | 169 | 173 | 178 | 182 | 187 | 192 | 196
| 4.5 | 210 | 218 | 225 | 232 | 239 | 246 | 253 | 260 | 267 | 274 | 281 | 288 | 295 | 302 | 309 | 316 | 323
| 5 | 317 | 327 | 337 | 347 | 357 | 367 | 377 | 387 | 397 | 407 | 417 | 427 | 437 | 447 | 457 | 467 | 477
| 5.5 | 442 | 456 | 469 | 483 | 496 | 510 | 523 | 537 | 550 | 564 | 577 | 590 | 604 | 617 | 631 | 644 | 657
| 6 | 589 | 607 | 624 | 642 | 659 | 677 | 694 | 712 | 729 | 746 | 764 | 781 | 799 | 816 | 833 | 851 | 868
| 6.5 | 760 | 783 | 805 | 827 | 849 | 871 | 893 | 915 | 937 | 959 | 981 | 1003 | 1025 | 1047 | 1069 | 1091 | 1113
| 7 | 958 | 986 | 1013 | 1041 | 1068 | 1096 | 1123 | 1151 | 1178 | 1205 | 1233 | 1260 | 1287 | 1314 | 1342 | 1369 | 1396
| 7.5 | 1186 | 1219 | 1253 | 1287 | 1320 | 1354 | 1387 | 1420 | 1454 | 1487 | 1520 | 1554 | 1587 | 1620 | 1653 | 1687 | 1720
| 8 | 1444 | 1485 | 1525 | 1565 | 1606 | 1646 | 1686 | 1727 | 1767 | 1807 | 1847 | 1887 | 1927 | 1967 | 2007 | 2046 | 2086
| 8.5 | 1731 | 1779 | 1827 | 1875 | 1922 | 1970 | 2018 | 2065 | 2113 | 2160 | 2208 | 2255 | 2302 | 2349 | 2396 | 2442 | 2489
| 9 | 2039 | 2095 | 2151 | 2207 | 2262 | 2317 | 2373 | 2428 | 2482 | 2537 | 2591 | 2645 | 2700 | 2754 | 2809 | 2863 | 2917
| 9.5 | 2363 | 2426 | 2490 | 2553 | 2616 | 2679 | 2741 | 2803 | 2866 | 2927 | 2989 | 3050 | 3105 | 3153 | 3201 | 3249 | 3297
| 10 | 2695 | 2766 | 2837 | 2907 | 2977 | 3046 | 3115 | 3174 | 3228 | 3281 | 3333 | 3386 | 3431 | 3468 | 3504 | 3540 | 3576
| 10.5 | 3030 | 3107 | 3183 | 3243 | 3302 | 3360 | 3418 | 3465 | 3506 | 3547 | 3587 | 3627 | 3661 | 3686 | 3712 | 3737 | 3761
| 11 | 3329 | 3392 | 3456 | 3503 | 3548 | 3593 | 3638 | 3673 | 3701 | 3730 | 3758 | 3786 | 3808 | 3823 | 3837 | 3851 | 3864
| 11.5 | 3556 | 3606 | 3656 | 3690 | 3722 | 3754 | 3786 | 3809 | 3826 | 3843 | 3859 | 3876 | 3886 | 3889 | 3892 | 3895 | 3897
| 12 | 3720 | 3756 | 3792 | 3813 | 3833 | 3853 | 3873 | 3883 | 3887 | 3892 | 3896 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900
| 12.5 | 3827 | 3850 | 3873 | 3881 | 3887 | 3894 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900
| 13 | 3884 | 3893 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900
| 13.5 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900
| 14 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900
| 14.5 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900
| 15 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900
| 15.5 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900
| 16 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900
| 16.5 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900
| 17 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900
| 17.5 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900
| 18 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900
| 18.5 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900
| 19 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900
| 19.5 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900
| 20 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900 | 3900
| 20.5 | 3861 | 3861 | 3861 | 3861 | 3861 | 3861 | 3861 | 3861 | 3861 | 3861 | 3861 | 3861 | 3861 | 3861 | 3861 | 3861 | 3861
| 21 | 3771 | 3771 | 3771 | 3771 | 3771 | 3771 | 3771 | 3771 | 3771 | 3771 | 3771 | 3771 | 3771 | 3771 | 3771 | 3771 | 3771
| 21.5 | 3592 | 3592 | 3592 | 3592 | 3592 | 3592 | 3592 | 3592 | 3592 | 3592 | 3592 | 3592 | 3592 | 3592 | 3592 | 3592 | 3592
| 22 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327
| 22.5 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003
| 23 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906
| 23.5 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874
| 24 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855
| 24.5 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835
| 25 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.62639 | 0.62639 | 0.62639 | 0.62639 | 0.62708 | 0.62778 | 0.62847 | 0.62917 | 0.62986 | 0.62986 | 0.63125 | 0.63194 | 0.63194 | 0.63264 | 0.63333 | 0.63333 | 0.63403
| 3.5 | 0.62083 | 0.62153 | 0.62222 | 0.62292 | 0.62292 | 0.62361 | 0.62431 | 0.62431 | 0.625 | 0.62569 | 0.62569 | 0.62639 | 0.62639 | 0.62708 | 0.62708 | 0.62778 | 0.62778
| 4 | 0.61597 | 0.61597 | 0.61667 | 0.61667 | 0.61736 | 0.61736 | 0.61736 | 0.61806 | 0.61806 | 0.61806 | 0.61875 | 0.61875 | 0.61875 | 0.61875 | 0.61944 | 0.61944 | 0.61944
| 4.5 | 0.61042 | 0.61042 | 0.61111 | 0.61111 | 0.61111 | 0.61111 | 0.61111 | 0.61111 | 0.61111 | 0.61111 | 0.61111 | 0.61111 | 0.61181 | 0.61181 | 0.61181 | 0.61181 | 0.61181
| 5 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60486 | 0.60486 | 0.60486 | 0.60486 | 0.60486 | 0.60486 | 0.60486 | 0.60486 | 0.60486 | 0.60486 | 0.60486 | 0.60486
| 5.5 | 0.59931 | 0.59931 | 0.59861 | 0.59861 | 0.59861 | 0.59861 | 0.59792 | 0.59792 | 0.59792 | 0.59792 | 0.59722 | 0.59722 | 0.59722 | 0.59722 | 0.59722 | 0.59722 | 0.59722
| 6 | 0.59514 | 0.59514 | 0.59444 | 0.59444 | 0.59444 | 0.59375 | 0.59375 | 0.59375 | 0.59306 | 0.59306 | 0.59306 | 0.59306 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59167
| 6.5 | 0.59306 | 0.59306 | 0.59236 | 0.59236 | 0.59236 | 0.59167 | 0.59167 | 0.59167 | 0.59167 | 0.59167 | 0.59097 | 0.59097 | 0.59097 | 0.59097 | 0.59028 | 0.59028 | 0.59028
| 7 | 0.59167 | 0.59097 | 0.59097 | 0.59097 | 0.59028 | 0.59028 | 0.59028 | 0.59028 | 0.59028 | 0.58958 | 0.58958 | 0.58958 | 0.58958 | 0.58958 | 0.58889 | 0.58889 | 0.58889
| 7.5 | 0.59028 | 0.58958 | 0.58958 | 0.58958 | 0.58889 | 0.58889 | 0.58889 | 0.58889 | 0.58889 | 0.58889 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.5875 | 0.5875
| 8 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.5875 | 0.5875 | 0.5875 | 0.5875 | 0.5875 | 0.5875 | 0.5875 | 0.5875 | 0.58681 | 0.58681 | 0.58681 | 0.58681
| 8.5 | 0.57014 | 0.57014 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944
| 9 | 0.55139 | 0.55139 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069
| 9.5 | 0.52431 | 0.52361 | 0.52361 | 0.52361 | 0.52292 | 0.52292 | 0.52292 | 0.52222 | 0.52222 | 0.52153 | 0.52153 | 0.52083 | 0.52014 | 0.51944 | 0.51944 | 0.51875 | 0.51806
| 10 | 0.49583 | 0.49514 | 0.49444 | 0.49375 | 0.49306 | 0.49236 | 0.49167 | 0.49097 | 0.49028 | 0.48889 | 0.48819 | 0.48681 | 0.48542 | 0.48403 | 0.48264 | 0.48125 | 0.47917
| 10.5 | 0.46875 | 0.46806 | 0.46667 | 0.46597 | 0.46528 | 0.46389 | 0.46319 | 0.46181 | 0.46042 | 0.45903 | 0.45764 | 0.45556 | 0.44722 | 0.43194 | 0.41806 | 0.40556 | 0.39444
| 11 | 0.44375 | 0.44236 | 0.44167 | 0.44028 | 0.43889 | 0.4375 | 0.43611 | 0.425 | 0.40972 | 0.39583 | 0.38403 | 0.37222 | 0.3625 | 0.35278 | 0.34375 | 0.33542 | 0.32708
| 11.5 | 0.42014 | 0.41875 | 0.41806 | 0.40208 | 0.38681 | 0.37361 | 0.36111 | 0.35 | 0.34028 | 0.33056 | 0.32153 | 0.31319 | 0.30556 | 0.29861 | 0.29167 | 0.28472 | 0.27847
| 12 | 0.375 | 0.36042 | 0.34792 | 0.33611 | 0.32569 | 0.31597 | 0.30694 | 0.29861 | 0.29028 | 0.28264 | 0.27569 | 0.26944 | 0.26319 | 0.25694 | 0.25139 | 0.24583 | 0.24097
| 12.5 | 0.31806 | 0.30764 | 0.29792 | 0.28889 | 0.28056 | 0.27292 | 0.26528 | 0.25833 | 0.25208 | 0.24583 | 0.23958 | 0.23472 | 0.22917 | 0.22431 | 0.21944 | 0.21528 | 0.21042
| 13 | 0.27569 | 0.26736 | 0.25972 | 0.25208 | 0.24514 | 0.23819 | 0.23194 | 0.22639 | 0.22083 | 0.21597 | 0.21111 | 0.20625 | 0.20139 | 0.19722 | 0.19306 | 0.18958 | 0.18611
| 13.5 | 0.24236 | 0.23472 | 0.22847 | 0.22222 | 0.21597 | 0.21042 | 0.20556 | 0.2 | 0.19583 | 0.19097 | 0.18681 | 0.18264 | 0.17917 | 0.175 | 0.17153 | 0.16806 | 0.16528
| 14 | 0.21458 | 0.20833 | 0.20278 | 0.19722 | 0.19236 | 0.1875 | 0.18264 | 0.17847 | 0.17431 | 0.17014 | 0.16667 | 0.16319 | 0.15972 | 0.15625 | 0.15347 | 0.15069 | 0.14792
| 14.5 | 0.19167 | 0.18611 | 0.18125 | 0.17639 | 0.17222 | 0.16806 | 0.16389 | 0.15972 | 0.15625 | 0.15278 | 0.14931 | 0.14653 | 0.14375 | 0.14028 | 0.13819 | 0.13542 | 0.13264
| 15 | 0.17222 | 0.16736 | 0.16319 | 0.15833 | 0.15486 | 0.15069 | 0.14722 | 0.14444 | 0.14097 | 0.1375 | 0.13472 | 0.13194 | 0.12986 | 0.12708 | 0.12431 | 0.12222 | 0.12014
| 15.5 | 0.15556 | 0.15139 | 0.14722 | 0.14375 | 0.14028 | 0.13681 | 0.13333 | 0.13056 | 0.12778 | 0.125 | 0.12222 | 0.12014 | 0.11736 | 0.11528 | 0.11319 | 0.11111 | 0.10903
| 16 | 0.14097 | 0.1375 | 0.13403 | 0.13056 | 0.12708 | 0.12431 | 0.12153 | 0.11875 | 0.11597 | 0.11389 | 0.11111 | 0.10903 | 0.10694 | 0.10486 | 0.10278 | 0.10139 | 0.099306
| 16.5 | 0.12847 | 0.125 | 0.12222 | 0.11875 | 0.11597 | 0.11319 | 0.11111 | 0.10833 | 0.10625 | 0.10417 | 0.10208 | 0.1 | 0.097917 | 0.095833 | 0.094444 | 0.092361 | 0.090972
| 17 | 0.11736 | 0.11458 | 0.11181 | 0.10903 | 0.10625 | 0.10417 | 0.10139 | 0.099306 | 0.097222 | 0.095139 | 0.093056 | 0.091667 | 0.089583 | 0.088194 | 0.086806 | 0.085417 | 0.083333
| 17.5 | 0.10764 | 0.10486 | 0.10278 | 0.1 | 0.097917 | 0.095833 | 0.093056 | 0.091667 | 0.089583 | 0.0875 | 0.086111 | 0.084722 | 0.082639 | 0.08125 | 0.079861 | 0.078472 | 0.077083
| 18 | 0.099306 | 0.097222 | 0.094444 | 0.092361 | 0.090278 | 0.088194 | 0.086111 | 0.084722 | 0.082639 | 0.08125 | 0.079167 | 0.077778 | 0.076389 | 0.075 | 0.073611 | 0.072222 | 0.071528
| 18.5 | 0.091667 | 0.089583 | 0.0875 | 0.085417 | 0.083333 | 0.08125 | 0.079861 | 0.077778 | 0.076389 | 0.075 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.097 | 0.095
| 19 | 0.084722 | 0.082639 | 0.08125 | 0.079167 | 0.077083 | 0.075694 | 0.074306 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.095 | 0.093 | 0.092 | 0.09 | 0.088
| 19.5 | 0.079167 | 0.077083 | 0.075 | 0.073611 | 0.072222 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.092 | 0.09 | 0.088 | 0.087 | 0.085 | 0.084 | 0.082
| 20 | 0.073611 | 0.071528 | 0.070139 | 0.099 | 0.096 | 0.094 | 0.092 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084 | 0.082 | 0.081 | 0.08 | 0.078 | 0.077
| 20.5 | 0.098 | 0.095 | 0.093 | 0.092 | 0.089 | 0.087 | 0.085 | 0.084 | 0.082 | 0.08 | 0.08 | 0.078 | 0.076 | 0.075 | 0.074 | 0.072 | 0.071
| 21 | 0.089 | 0.087 | 0.085 | 0.084 | 0.081 | 0.079 | 0.078 | 0.077 | 0.075 | 0.073 | 0.073 | 0.071 | 0.069 | 0.068 | 0.068 | 0.066 | 0.065
| 21.5 | 0.08 | 0.078 | 0.076 | 0.075 | 0.072 | 0.071 | 0.069 | 0.069 | 0.067 | 0.066 | 0.065 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058
| 22 | 0.07 | 0.068 | 0.066 | 0.065 | 0.063 | 0.062 | 0.06 | 0.06 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.051
| 22.5 | 0.059 | 0.058 | 0.057 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.045 | 0.044 | 0.043
| 23 | 0.054 | 0.053 | 0.052 | 0.051 | 0.049 | 0.048 | 0.047 | 0.047 | 0.045 | 0.044 | 0.044 | 0.043 | 0.042 | 0.041 | 0.041 | 0.04 | 0.039
| 23.5 | 0.051 | 0.05 | 0.049 | 0.048 | 0.046 | 0.045 | 0.044 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.039 | 0.038 | 0.037
| 24 | 0.048 | 0.047 | 0.046 | 0.045 | 0.043 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036 | 0.035 | 0.035
| 24.5 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.033
| 25 | 0.042 | 0.041 | 0.04 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032 | 0.032 | 0.032 | 0.031 | 0.03