## Sheet1
PROPERTIES
General
Name | Nordex N131/3.9 Mode 1 3,8MW
Manufacturer | Nordex
Hub Height | 84 | 114 | 120 | 134 | 164
Power
Rated Power | 3800
Peak Power | 3800
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 131
Number of blades | 3
Rated RPM | 12.6
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 25
Restart Wind Speed | 19.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 40
High Temperature Restart | 38
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | III
Turbine SubClass | S
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 40
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 1 | 3 | 4 | 5 | 7 | 8 | 9 | 10 | 12 | 13 | 14 | 15 | 17 | 18 | 19 | 21 | 22
| 3.5 | 52 | 55 | 58 | 61 | 63 | 66 | 69 | 71 | 74 | 77 | 79 | 82 | 85 | 87 | 90 | 93 | 95
| 4 | 122 | 127 | 132 | 136 | 141 | 146 | 150 | 155 | 159 | 164 | 169 | 173 | 178 | 182 | 187 | 192 | 196
| 4.5 | 210 | 218 | 225 | 232 | 239 | 246 | 253 | 260 | 267 | 274 | 281 | 288 | 295 | 302 | 309 | 316 | 323
| 5 | 317 | 327 | 337 | 347 | 357 | 367 | 377 | 387 | 397 | 407 | 417 | 427 | 437 | 447 | 457 | 467 | 477
| 5.5 | 442 | 456 | 469 | 483 | 496 | 510 | 523 | 537 | 550 | 563 | 577 | 590 | 604 | 617 | 631 | 644 | 657
| 6 | 589 | 607 | 624 | 642 | 659 | 677 | 694 | 711 | 729 | 746 | 764 | 781 | 799 | 816 | 833 | 851 | 868
| 6.5 | 760 | 783 | 805 | 827 | 849 | 871 | 893 | 915 | 937 | 959 | 981 | 1003 | 1025 | 1047 | 1069 | 1091 | 1113
| 7 | 958 | 986 | 1013 | 1041 | 1068 | 1096 | 1123 | 1151 | 1178 | 1205 | 1233 | 1260 | 1287 | 1314 | 1342 | 1369 | 1396
| 7.5 | 1186 | 1219 | 1253 | 1287 | 1320 | 1353 | 1387 | 1420 | 1454 | 1487 | 1520 | 1554 | 1587 | 1620 | 1653 | 1686 | 1719
| 8 | 1444 | 1485 | 1525 | 1565 | 1606 | 1646 | 1686 | 1727 | 1767 | 1807 | 1847 | 1887 | 1927 | 1967 | 2007 | 2047 | 2086
| 8.5 | 1730 | 1778 | 1826 | 1874 | 1922 | 1969 | 2017 | 2064 | 2112 | 2159 | 2207 | 2254 | 2301 | 2347 | 2394 | 2441 | 2487
| 9 | 2037 | 2093 | 2148 | 2204 | 2259 | 2314 | 2369 | 2424 | 2479 | 2533 | 2587 | 2641 | 2696 | 2751 | 2805 | 2859 | 2912
| 9.5 | 2357 | 2421 | 2484 | 2547 | 2609 | 2672 | 2734 | 2797 | 2859 | 2920 | 2981 | 3036 | 3085 | 3133 | 3181 | 3228 | 3276
| 10 | 2685 | 2756 | 2826 | 2896 | 2966 | 3035 | 3096 | 3150 | 3203 | 3256 | 3309 | 3353 | 3390 | 3427 | 3463 | 3499 | 3535
| 10.5 | 3014 | 3091 | 3156 | 3215 | 3273 | 3331 | 3381 | 3422 | 3463 | 3503 | 3543 | 3577 | 3602 | 3628 | 3653 | 3678 | 3702
| 11 | 3296 | 3359 | 3411 | 3457 | 3502 | 3547 | 3584 | 3613 | 3642 | 3671 | 3699 | 3721 | 3735 | 3749 | 3763 | 3777 | 3791
| 11.5 | 3508 | 3558 | 3597 | 3629 | 3662 | 3694 | 3719 | 3736 | 3753 | 3770 | 3786 | 3796 | 3799 | 3802 | 3805 | 3808 | 3810
| 12 | 3658 | 3695 | 3720 | 3740 | 3760 | 3780 | 3792 | 3797 | 3802 | 3806 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810
| 12.5 | 3754 | 3777 | 3789 | 3796 | 3803 | 3809 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810
| 13 | 3800 | 3809 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810
| 13.5 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810
| 14 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810
| 14.5 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810
| 15 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810
| 15.5 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810
| 16 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810
| 16.5 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810
| 17 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810
| 17.5 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810
| 18 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810
| 18.5 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810
| 19 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810
| 19.5 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810
| 20 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810
| 20.5 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810 | 3810
| 21 | 3743 | 3743 | 3743 | 3743 | 3743 | 3743 | 3743 | 3743 | 3743 | 3743 | 3743 | 3743 | 3743 | 3743 | 3743 | 3743 | 3743
| 21.5 | 3592 | 3592 | 3592 | 3592 | 3592 | 3592 | 3592 | 3592 | 3592 | 3592 | 3592 | 3592 | 3592 | 3592 | 3592 | 3592 | 3592
| 22 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327
| 22.5 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003
| 23 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906
| 23.5 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874
| 24 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855
| 24.5 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835
| 25 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.62639 | 0.62639 | 0.62639 | 0.62639 | 0.62708 | 0.62778 | 0.62847 | 0.62917 | 0.62986 | 0.63056 | 0.63056 | 0.63194 | 0.63194 | 0.63264 | 0.63333 | 0.63403 | 0.63403
| 3.5 | 0.62083 | 0.62153 | 0.62222 | 0.62292 | 0.62292 | 0.62361 | 0.62431 | 0.625 | 0.625 | 0.62569 | 0.62569 | 0.62639 | 0.62639 | 0.62708 | 0.62708 | 0.62778 | 0.62778
| 4 | 0.61597 | 0.61597 | 0.61667 | 0.61667 | 0.61736 | 0.61736 | 0.61736 | 0.61806 | 0.61806 | 0.61806 | 0.61875 | 0.61875 | 0.61875 | 0.61944 | 0.61944 | 0.61944 | 0.61944
| 4.5 | 0.61042 | 0.61111 | 0.61111 | 0.61111 | 0.61111 | 0.61111 | 0.61111 | 0.61111 | 0.61111 | 0.61181 | 0.61181 | 0.61181 | 0.61181 | 0.61181 | 0.61181 | 0.61181 | 0.61181
| 5 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60486 | 0.60486 | 0.60486 | 0.60486 | 0.60486 | 0.60486 | 0.60486 | 0.60486 | 0.60486
| 5.5 | 0.59931 | 0.59931 | 0.59931 | 0.59861 | 0.59861 | 0.59861 | 0.59861 | 0.59861 | 0.59792 | 0.59792 | 0.59792 | 0.59792 | 0.59722 | 0.59722 | 0.59722 | 0.59722 | 0.59722
| 6 | 0.59514 | 0.59514 | 0.59514 | 0.59444 | 0.59444 | 0.59444 | 0.59375 | 0.59375 | 0.59375 | 0.59306 | 0.59306 | 0.59306 | 0.59306 | 0.59306 | 0.59236 | 0.59236 | 0.59236
| 6.5 | 0.59306 | 0.59306 | 0.59306 | 0.59236 | 0.59236 | 0.59236 | 0.59167 | 0.59167 | 0.59167 | 0.59167 | 0.59167 | 0.59097 | 0.59097 | 0.59097 | 0.59097 | 0.59097 | 0.59028
| 7 | 0.59167 | 0.59167 | 0.59097 | 0.59097 | 0.59097 | 0.59028 | 0.59028 | 0.59028 | 0.59028 | 0.59028 | 0.59028 | 0.58958 | 0.58958 | 0.58958 | 0.58958 | 0.58958 | 0.58889
| 7.5 | 0.59028 | 0.59028 | 0.58958 | 0.58958 | 0.58958 | 0.58958 | 0.58889 | 0.58889 | 0.58889 | 0.58889 | 0.58889 | 0.58889 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819
| 8 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.5875 | 0.5875 | 0.5875 | 0.5875 | 0.5875 | 0.5875 | 0.5875 | 0.5875 | 0.58681 | 0.58681
| 8.5 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944
| 9 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069
| 9.5 | 0.51944 | 0.51944 | 0.51875 | 0.51875 | 0.51806 | 0.51806 | 0.51736 | 0.51667 | 0.51667 | 0.51597 | 0.51528 | 0.51458 | 0.51389 | 0.51319 | 0.5125 | 0.51181 | 0.51042
| 10 | 0.49097 | 0.49028 | 0.49028 | 0.48889 | 0.48889 | 0.4875 | 0.48681 | 0.48611 | 0.48542 | 0.48472 | 0.48333 | 0.48194 | 0.48125 | 0.47986 | 0.47778 | 0.47639 | 0.475
| 10.5 | 0.46389 | 0.46319 | 0.4625 | 0.46181 | 0.46042 | 0.45972 | 0.45833 | 0.45764 | 0.45625 | 0.45486 | 0.45347 | 0.44444 | 0.42917 | 0.41458 | 0.40208 | 0.39097 | 0.38056
| 11 | 0.43889 | 0.43819 | 0.43681 | 0.43611 | 0.43472 | 0.43403 | 0.42431 | 0.40903 | 0.39514 | 0.38194 | 0.37083 | 0.35972 | 0.35 | 0.34097 | 0.33264 | 0.32431 | 0.31667
| 11.5 | 0.41597 | 0.41458 | 0.40278 | 0.3875 | 0.37361 | 0.36111 | 0.34931 | 0.33889 | 0.32917 | 0.32014 | 0.31181 | 0.30417 | 0.29653 | 0.28958 | 0.28264 | 0.27639 | 0.27014
| 12 | 0.3625 | 0.34861 | 0.33681 | 0.32569 | 0.31528 | 0.30625 | 0.29722 | 0.28958 | 0.28194 | 0.27431 | 0.26806 | 0.26111 | 0.25556 | 0.25 | 0.24444 | 0.23889 | 0.23403
| 12.5 | 0.30833 | 0.29861 | 0.28889 | 0.28056 | 0.27222 | 0.26458 | 0.25764 | 0.25069 | 0.24444 | 0.23889 | 0.23333 | 0.22778 | 0.22292 | 0.21806 | 0.21319 | 0.20903 | 0.20486
| 13 | 0.26806 | 0.25972 | 0.25208 | 0.24514 | 0.23819 | 0.23194 | 0.22569 | 0.22014 | 0.21458 | 0.20972 | 0.20486 | 0.20069 | 0.19583 | 0.19167 | 0.18819 | 0.18472 | 0.18056
| 13.5 | 0.23542 | 0.22847 | 0.22222 | 0.21597 | 0.21042 | 0.20486 | 0.2 | 0.19444 | 0.19028 | 0.18611 | 0.18194 | 0.17778 | 0.17431 | 0.17083 | 0.16736 | 0.16389 | 0.16111
| 14 | 0.20903 | 0.20278 | 0.19722 | 0.19167 | 0.18681 | 0.18194 | 0.17778 | 0.17361 | 0.16944 | 0.16597 | 0.1625 | 0.15903 | 0.15556 | 0.15278 | 0.14931 | 0.14653 | 0.14375
| 14.5 | 0.18681 | 0.18125 | 0.17639 | 0.17153 | 0.16736 | 0.16319 | 0.15972 | 0.15556 | 0.15208 | 0.14861 | 0.14583 | 0.14236 | 0.13958 | 0.13681 | 0.13472 | 0.13194 | 0.12917
| 15 | 0.16736 | 0.16319 | 0.15833 | 0.15486 | 0.15069 | 0.14722 | 0.14375 | 0.14028 | 0.1375 | 0.13403 | 0.13125 | 0.12917 | 0.12639 | 0.12361 | 0.12153 | 0.11944 | 0.11667
| 15.5 | 0.15139 | 0.14722 | 0.14375 | 0.13958 | 0.13611 | 0.13333 | 0.12986 | 0.12708 | 0.12431 | 0.12153 | 0.11944 | 0.11667 | 0.11458 | 0.1125 | 0.11042 | 0.10833 | 0.10625
| 16 | 0.1375 | 0.13403 | 0.13056 | 0.12708 | 0.12431 | 0.12083 | 0.11806 | 0.11597 | 0.11319 | 0.11111 | 0.10833 | 0.10625 | 0.10417 | 0.10208 | 0.10069 | 0.098611 | 0.097222
| 16.5 | 0.125 | 0.12222 | 0.11875 | 0.11597 | 0.11319 | 0.11042 | 0.10833 | 0.10556 | 0.10347 | 0.10139 | 0.099306 | 0.097222 | 0.095833 | 0.09375 | 0.091667 | 0.090278 | 0.088889
| 17 | 0.11458 | 0.11181 | 0.10903 | 0.10625 | 0.10347 | 0.10139 | 0.099306 | 0.097222 | 0.095139 | 0.093056 | 0.090972 | 0.089583 | 0.0875 | 0.086111 | 0.084722 | 0.083333 | 0.081944
| 17.5 | 0.10556 | 0.10278 | 0.1 | 0.097222 | 0.095139 | 0.093056 | 0.090972 | 0.088889 | 0.0875 | 0.085417 | 0.084028 | 0.081944 | 0.080556 | 0.079167 | 0.077778 | 0.076389 | 0.075
| 18 | 0.097222 | 0.094444 | 0.092361 | 0.090278 | 0.088194 | 0.086111 | 0.084028 | 0.081944 | 0.080556 | 0.079167 | 0.077778 | 0.075694 | 0.074306 | 0.073611 | 0.072222 | 0.070833 | 0.069444
| 18.5 | 0.089583 | 0.0875 | 0.085417 | 0.083333 | 0.08125 | 0.079167 | 0.077778 | 0.076389 | 0.075 | 0.072917 | 0.071528 | 0.070139 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.093
| 19 | 0.083333 | 0.080556 | 0.079167 | 0.077083 | 0.075694 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092 | 0.091 | 0.089 | 0.088 | 0.086
| 19.5 | 0.077083 | 0.075 | 0.073611 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.088 | 0.086 | 0.085 | 0.083 | 0.082 | 0.08
| 20 | 0.071528 | 0.070139 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.087 | 0.085 | 0.083 | 0.082 | 0.08 | 0.079 | 0.078 | 0.076 | 0.075
| 20.5 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.085 | 0.083 | 0.081 | 0.08 | 0.079 | 0.077 | 0.076 | 0.074 | 0.073 | 0.072 | 0.07 | 0.069
| 21 | 0.087 | 0.085 | 0.083 | 0.081 | 0.079 | 0.078 | 0.076 | 0.074 | 0.073 | 0.072 | 0.07 | 0.069 | 0.068 | 0.067 | 0.066 | 0.064 | 0.063
| 21.5 | 0.078 | 0.076 | 0.074 | 0.072 | 0.071 | 0.069 | 0.068 | 0.066 | 0.066 | 0.064 | 0.062 | 0.062 | 0.06 | 0.059 | 0.059 | 0.057 | 0.056
| 22 | 0.068 | 0.066 | 0.064 | 0.063 | 0.062 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056 | 0.054 | 0.054 | 0.052 | 0.052 | 0.051 | 0.05 | 0.049
| 22.5 | 0.058 | 0.057 | 0.055 | 0.054 | 0.053 | 0.052 | 0.05 | 0.049 | 0.049 | 0.048 | 0.046 | 0.046 | 0.045 | 0.044 | 0.044 | 0.043 | 0.042
| 23 | 0.053 | 0.052 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038
| 23.5 | 0.05 | 0.049 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037 | 0.036
| 24 | 0.047 | 0.046 | 0.044 | 0.043 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.034
| 24.5 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.032
| 25 | 0.041 | 0.04 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032 | 0.032 | 0.031 | 0.031 | 0.03 | 0.03