## Sheet1
PROPERTIES
General
Name | Nordex N131/3.9 Mode 12 2,67MW
Manufacturer | Nordex
Hub Height | 84 | 114 | 120 | 134 | 164
Power
Rated Power | 2670
Peak Power | 2670
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 131
Number of blades | 3
Rated RPM | 12.6
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 25
Restart Wind Speed | 19.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 40
High Temperature Restart | 38
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | III
Turbine SubClass | S
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 40
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 1 | 3 | 4 | 5 | 7 | 8 | 9 | 10 | 12 | 13 | 14 | 15 | 17 | 18 | 19 | 21 | 22
| 3.5 | 52 | 55 | 58 | 60 | 63 | 66 | 69 | 71 | 74 | 77 | 79 | 82 | 85 | 87 | 90 | 93 | 95
| 4 | 122 | 127 | 132 | 136 | 141 | 145 | 150 | 155 | 159 | 164 | 169 | 173 | 178 | 182 | 187 | 192 | 196
| 4.5 | 210 | 217 | 224 | 232 | 239 | 246 | 253 | 260 | 267 | 274 | 281 | 288 | 295 | 302 | 309 | 316 | 323
| 5 | 317 | 327 | 337 | 347 | 357 | 367 | 377 | 387 | 397 | 407 | 417 | 426 | 436 | 446 | 456 | 466 | 476
| 5.5 | 442 | 455 | 469 | 482 | 496 | 509 | 523 | 536 | 549 | 563 | 576 | 590 | 603 | 617 | 630 | 643 | 657
| 6 | 590 | 607 | 625 | 642 | 659 | 677 | 694 | 712 | 729 | 747 | 764 | 781 | 799 | 816 | 834 | 851 | 868
| 6.5 | 756 | 778 | 800 | 823 | 845 | 867 | 889 | 911 | 933 | 955 | 977 | 999 | 1021 | 1043 | 1065 | 1087 | 1109
| 7 | 932 | 959 | 987 | 1014 | 1041 | 1068 | 1095 | 1122 | 1150 | 1177 | 1205 | 1232 | 1260 | 1287 | 1315 | 1341 | 1369
| 7.5 | 1109 | 1142 | 1175 | 1207 | 1240 | 1272 | 1304 | 1337 | 1370 | 1404 | 1437 | 1470 | 1504 | 1537 | 1570 | 1602 | 1636
| 8 | 1284 | 1322 | 1361 | 1399 | 1437 | 1474 | 1511 | 1550 | 1589 | 1629 | 1669 | 1707 | 1748 | 1787 | 1826 | 1863 | 1902
| 8.5 | 1457 | 1500 | 1545 | 1588 | 1631 | 1673 | 1715 | 1760 | 1806 | 1852 | 1898 | 1942 | 1989 | 2035 | 2081 | 2124 | 2168
| 9 | 1629 | 1676 | 1727 | 1775 | 1824 | 1871 | 1918 | 1969 | 2020 | 2072 | 2125 | 2176 | 2226 | 2268 | 2310 | 2350 | 2387
| 9.5 | 1798 | 1851 | 1907 | 1960 | 2015 | 2066 | 2118 | 2174 | 2232 | 2282 | 2329 | 2374 | 2415 | 2446 | 2477 | 2507 | 2534
| 10 | 1965 | 2022 | 2083 | 2142 | 2201 | 2258 | 2308 | 2356 | 2406 | 2445 | 2480 | 2514 | 2544 | 2566 | 2587 | 2608 | 2625
| 10.5 | 2128 | 2190 | 2256 | 2317 | 2367 | 2414 | 2455 | 2492 | 2530 | 2558 | 2583 | 2606 | 2626 | 2637 | 2649 | 2660 | 2667
| 11 | 2287 | 2349 | 2403 | 2454 | 2492 | 2529 | 2558 | 2584 | 2611 | 2629 | 2643 | 2656 | 2665 | 2667 | 2668 | 2670 | 2670
| 11.5 | 2421 | 2470 | 2513 | 2552 | 2579 | 2606 | 2626 | 2641 | 2657 | 2664 | 2667 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670
| 12 | 2521 | 2559 | 2590 | 2618 | 2635 | 2652 | 2662 | 2666 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670
| 12.5 | 2592 | 2620 | 2640 | 2657 | 2663 | 2669 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670
| 13 | 2639 | 2656 | 2664 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670
| 13.5 | 2664 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670
| 14 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670
| 14.5 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670
| 15 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670
| 15.5 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670
| 16 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670
| 16.5 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670
| 17 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670
| 17.5 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670
| 18 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670
| 18.5 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670
| 19 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670
| 19.5 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670
| 20 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670
| 20.5 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670
| 21 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670
| 21.5 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670
| 22 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670 | 2670

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.62639 | 0.62639 | 0.62639 | 0.62639 | 0.62708 | 0.62778 | 0.62847 | 0.62917 | 0.62986 | 0.63056 | 0.63125 | 0.63194 | 0.63264 | 0.63264 | 0.63333 | 0.63403 | 0.63403
| 3.5 | 0.62153 | 0.62222 | 0.62292 | 0.62361 | 0.62431 | 0.625 | 0.625 | 0.62569 | 0.62639 | 0.62639 | 0.62708 | 0.62708 | 0.62778 | 0.62778 | 0.62847 | 0.62847 | 0.62917
| 4 | 0.61736 | 0.61806 | 0.61806 | 0.61875 | 0.61875 | 0.61944 | 0.61944 | 0.61944 | 0.62014 | 0.62014 | 0.62014 | 0.62083 | 0.62083 | 0.62083 | 0.62083 | 0.62153 | 0.62153
| 4.5 | 0.61319 | 0.61319 | 0.61319 | 0.61319 | 0.61389 | 0.61389 | 0.61389 | 0.61389 | 0.61389 | 0.61389 | 0.61389 | 0.61389 | 0.61389 | 0.61458 | 0.61458 | 0.61458 | 0.61458
| 5 | 0.60833 | 0.60833 | 0.60833 | 0.60833 | 0.60833 | 0.60833 | 0.60833 | 0.60833 | 0.60833 | 0.60833 | 0.60833 | 0.60833 | 0.60833 | 0.60833 | 0.60833 | 0.60764 | 0.60764
| 5.5 | 0.60347 | 0.60278 | 0.60278 | 0.60278 | 0.60208 | 0.60208 | 0.60208 | 0.60139 | 0.60139 | 0.60139 | 0.60139 | 0.60139 | 0.60139 | 0.60069 | 0.60069 | 0.60069 | 0.60069
| 6 | 0.59931 | 0.59931 | 0.59931 | 0.59861 | 0.59861 | 0.59861 | 0.59792 | 0.59792 | 0.59792 | 0.59792 | 0.59722 | 0.59722 | 0.59722 | 0.59722 | 0.59722 | 0.59653 | 0.59653
| 6.5 | 0.57361 | 0.57361 | 0.57361 | 0.57431 | 0.57431 | 0.57431 | 0.575 | 0.575 | 0.575 | 0.57569 | 0.57569 | 0.57639 | 0.57639 | 0.57708 | 0.57708 | 0.57708 | 0.57708
| 7 | 0.52014 | 0.52083 | 0.52153 | 0.52222 | 0.52222 | 0.52292 | 0.52292 | 0.52361 | 0.52431 | 0.52569 | 0.52639 | 0.52708 | 0.52778 | 0.52917 | 0.52917 | 0.52986 | 0.53056
| 7.5 | 0.47292 | 0.47292 | 0.47431 | 0.475 | 0.47569 | 0.47639 | 0.47639 | 0.47778 | 0.47847 | 0.47986 | 0.48194 | 0.48264 | 0.48403 | 0.48472 | 0.48611 | 0.48611 | 0.4875
| 8 | 0.43056 | 0.43125 | 0.43264 | 0.43333 | 0.43472 | 0.43472 | 0.43542 | 0.43681 | 0.43819 | 0.43958 | 0.44167 | 0.44236 | 0.44444 | 0.44583 | 0.44722 | 0.44722 | 0.44931
| 8.5 | 0.39375 | 0.39444 | 0.39583 | 0.39722 | 0.39792 | 0.39861 | 0.39931 | 0.40069 | 0.40208 | 0.40417 | 0.40556 | 0.40694 | 0.40903 | 0.41042 | 0.41181 | 0.4125 | 0.41389
| 9 | 0.36181 | 0.3625 | 0.36389 | 0.36458 | 0.36597 | 0.36667 | 0.36667 | 0.36806 | 0.37014 | 0.37153 | 0.37361 | 0.375 | 0.37708 | 0.37847 | 0.37986 | 0.38056 | 0.38194
| 9.5 | 0.33264 | 0.33333 | 0.33472 | 0.33611 | 0.3375 | 0.3375 | 0.33819 | 0.33958 | 0.34097 | 0.34306 | 0.34514 | 0.34583 | 0.34792 | 0.34931 | 0.35139 | 0.35208 | 0.34861
| 10 | 0.30694 | 0.30764 | 0.30972 | 0.31042 | 0.31111 | 0.31181 | 0.3125 | 0.31389 | 0.31528 | 0.31667 | 0.31875 | 0.32083 | 0.31667 | 0.30764 | 0.29931 | 0.29167 | 0.28472
| 10.5 | 0.28403 | 0.28472 | 0.28611 | 0.28681 | 0.28819 | 0.28819 | 0.28889 | 0.29028 | 0.29306 | 0.28611 | 0.27778 | 0.27014 | 0.26319 | 0.25694 | 0.25069 | 0.24514 | 0.23958
| 11 | 0.26319 | 0.26389 | 0.26528 | 0.26597 | 0.26736 | 0.26875 | 0.26389 | 0.25556 | 0.24792 | 0.24167 | 0.23542 | 0.22986 | 0.22431 | 0.21944 | 0.21389 | 0.20972 | 0.20556
| 11.5 | 0.24444 | 0.24514 | 0.24792 | 0.24861 | 0.23889 | 0.23125 | 0.225 | 0.21875 | 0.21319 | 0.20764 | 0.20278 | 0.19792 | 0.19375 | 0.18958 | 0.18542 | 0.18194 | 0.17778
| 12 | 0.22917 | 0.22778 | 0.21944 | 0.21181 | 0.20556 | 0.2 | 0.19514 | 0.19028 | 0.18542 | 0.18056 | 0.17639 | 0.17292 | 0.16875 | 0.16528 | 0.16181 | 0.15903 | 0.15556
| 12.5 | 0.20347 | 0.19653 | 0.19028 | 0.18472 | 0.17986 | 0.175 | 0.17083 | 0.16667 | 0.1625 | 0.15903 | 0.15556 | 0.15208 | 0.14861 | 0.14583 | 0.14306 | 0.14028 | 0.1375
| 13 | 0.17778 | 0.17292 | 0.16806 | 0.16319 | 0.15903 | 0.15486 | 0.15139 | 0.14722 | 0.14375 | 0.14097 | 0.1375 | 0.13472 | 0.13194 | 0.12917 | 0.12639 | 0.12431 | 0.12222
| 13.5 | 0.15764 | 0.15347 | 0.14861 | 0.14514 | 0.14167 | 0.1375 | 0.13472 | 0.13125 | 0.12847 | 0.12569 | 0.12292 | 0.12014 | 0.11806 | 0.11528 | 0.11319 | 0.11111 | 0.10903
| 14 | 0.14097 | 0.13681 | 0.13333 | 0.12986 | 0.12639 | 0.12361 | 0.12014 | 0.11736 | 0.11528 | 0.1125 | 0.11042 | 0.10764 | 0.10556 | 0.10347 | 0.10139 | 0.1 | 0.097917
| 14.5 | 0.12639 | 0.12292 | 0.11944 | 0.11667 | 0.11389 | 0.11111 | 0.10833 | 0.10625 | 0.10347 | 0.10139 | 0.099306 | 0.097222 | 0.095139 | 0.09375 | 0.091667 | 0.090278 | 0.088194
| 15 | 0.11389 | 0.11111 | 0.10833 | 0.10556 | 0.10278 | 0.10069 | 0.097917 | 0.095833 | 0.09375 | 0.091667 | 0.090278 | 0.088194 | 0.086111 | 0.084722 | 0.083333 | 0.081944 | 0.080556
| 15.5 | 0.10347 | 0.10069 | 0.097917 | 0.095833 | 0.093056 | 0.090972 | 0.088889 | 0.0875 | 0.085417 | 0.083333 | 0.081944 | 0.080556 | 0.078472 | 0.077083 | 0.075694 | 0.074306 | 0.072917
| 16 | 0.094444 | 0.091667 | 0.089583 | 0.0875 | 0.085417 | 0.083333 | 0.08125 | 0.079861 | 0.077778 | 0.076389 | 0.075 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096
| 16.5 | 0.086111 | 0.084028 | 0.081944 | 0.079861 | 0.077778 | 0.076389 | 0.074306 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.092 | 0.09 | 0.088
| 17 | 0.079167 | 0.077083 | 0.075 | 0.073611 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084 | 0.083 | 0.082
| 17.5 | 0.072917 | 0.070833 | 0.069444 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084 | 0.082 | 0.081 | 0.079 | 0.078 | 0.076 | 0.075
| 18 | 0.097 | 0.094 | 0.092 | 0.09 | 0.088 | 0.086 | 0.084 | 0.082 | 0.081 | 0.079 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.071 | 0.07
| 18.5 | 0.09 | 0.087 | 0.085 | 0.083 | 0.082 | 0.08 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.071 | 0.069 | 0.068 | 0.067 | 0.066 | 0.065
| 19 | 0.083 | 0.081 | 0.079 | 0.077 | 0.076 | 0.074 | 0.072 | 0.071 | 0.07 | 0.068 | 0.067 | 0.066 | 0.065 | 0.064 | 0.062 | 0.061 | 0.06
| 19.5 | 0.077 | 0.076 | 0.074 | 0.072 | 0.07 | 0.069 | 0.068 | 0.066 | 0.065 | 0.064 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056
| 20 | 0.072 | 0.07 | 0.069 | 0.067 | 0.066 | 0.064 | 0.063 | 0.062 | 0.061 | 0.06 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.054 | 0.053
| 20.5 | 0.067 | 0.065 | 0.064 | 0.062 | 0.061 | 0.059 | 0.058 | 0.057 | 0.056 | 0.056 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.05 | 0.049
| 21 | 0.061 | 0.059 | 0.058 | 0.057 | 0.056 | 0.054 | 0.053 | 0.052 | 0.051 | 0.051 | 0.049 | 0.048 | 0.047 | 0.046 | 0.046 | 0.046 | 0.045
| 21.5 | 0.054 | 0.053 | 0.052 | 0.05 | 0.05 | 0.048 | 0.047 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.041 | 0.041 | 0.04
| 22 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.041 | 0.04 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036 | 0.035 | 0.035 | 0.035