## Sheet1
PROPERTIES
General
Name | Nordex N131/3.9 Mode 2 3,71MW
Manufacturer | Nordex
Hub Height | 84 | 114 | 120 | 134 | 164
Power
Rated Power | 3710
Peak Power | 3710
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 131
Number of blades | 3
Rated RPM | 12.6
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 25
Restart Wind Speed | 19.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 40
High Temperature Restart | 38
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | III
Turbine SubClass | S
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 40
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 1 | 3 | 4 | 5 | 7 | 8 | 9 | 10 | 12 | 13 | 14 | 15 | 17 | 18 | 19 | 21 | 22
| 3.5 | 52 | 55 | 58 | 61 | 63 | 66 | 69 | 71 | 74 | 77 | 79 | 82 | 85 | 87 | 90 | 93 | 95
| 4 | 122 | 127 | 132 | 136 | 141 | 146 | 150 | 155 | 159 | 164 | 169 | 173 | 178 | 182 | 187 | 192 | 196
| 4.5 | 210 | 218 | 225 | 232 | 239 | 246 | 253 | 260 | 267 | 274 | 281 | 288 | 295 | 302 | 309 | 316 | 323
| 5 | 317 | 327 | 337 | 347 | 357 | 367 | 377 | 387 | 397 | 407 | 417 | 427 | 437 | 447 | 457 | 467 | 477
| 5.5 | 442 | 456 | 469 | 483 | 496 | 510 | 523 | 537 | 550 | 563 | 577 | 590 | 604 | 617 | 631 | 644 | 657
| 6 | 589 | 607 | 624 | 642 | 659 | 677 | 694 | 711 | 729 | 746 | 764 | 781 | 799 | 816 | 833 | 851 | 868
| 6.5 | 760 | 782 | 805 | 827 | 849 | 871 | 893 | 915 | 937 | 959 | 981 | 1003 | 1025 | 1047 | 1069 | 1091 | 1113
| 7 | 958 | 986 | 1013 | 1041 | 1068 | 1096 | 1123 | 1150 | 1178 | 1205 | 1232 | 1260 | 1287 | 1314 | 1341 | 1369 | 1396
| 7.5 | 1186 | 1219 | 1253 | 1286 | 1320 | 1353 | 1387 | 1420 | 1454 | 1487 | 1520 | 1554 | 1587 | 1620 | 1653 | 1686 | 1719
| 8 | 1444 | 1484 | 1525 | 1565 | 1606 | 1646 | 1686 | 1726 | 1766 | 1806 | 1846 | 1886 | 1926 | 1966 | 2006 | 2046 | 2086
| 8.5 | 1729 | 1777 | 1825 | 1872 | 1920 | 1968 | 2015 | 2063 | 2110 | 2158 | 2205 | 2252 | 2298 | 2345 | 2392 | 2438 | 2485
| 9 | 2034 | 2089 | 2145 | 2200 | 2256 | 2311 | 2365 | 2420 | 2475 | 2529 | 2584 | 2639 | 2693 | 2748 | 2802 | 2856 | 2901
| 9.5 | 2351 | 2415 | 2478 | 2541 | 2604 | 2666 | 2729 | 2791 | 2853 | 2915 | 2967 | 3016 | 3064 | 3112 | 3160 | 3208 | 3242
| 10 | 2677 | 2747 | 2818 | 2888 | 2957 | 3018 | 3072 | 3126 | 3179 | 3232 | 3273 | 3310 | 3347 | 3383 | 3420 | 3456 | 3480
| 10.5 | 3001 | 3069 | 3128 | 3187 | 3246 | 3294 | 3336 | 3377 | 3418 | 3459 | 3488 | 3514 | 3539 | 3565 | 3590 | 3616 | 3629
| 11 | 3264 | 3318 | 3364 | 3410 | 3456 | 3492 | 3521 | 3550 | 3579 | 3608 | 3626 | 3641 | 3655 | 3670 | 3684 | 3698 | 3701
| 11.5 | 3459 | 3500 | 3533 | 3566 | 3598 | 3622 | 3640 | 3657 | 3674 | 3691 | 3697 | 3700 | 3703 | 3706 | 3709 | 3710 | 3710
| 12 | 3594 | 3621 | 3642 | 3662 | 3682 | 3693 | 3698 | 3703 | 3707 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710
| 12.5 | 3675 | 3690 | 3696 | 3703 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710
| 13 | 3708 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710
| 13.5 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710
| 14 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710
| 14.5 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710
| 15 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710
| 15.5 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710
| 16 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710
| 16.5 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710
| 17 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710
| 17.5 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710
| 18 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710
| 18.5 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710
| 19 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710
| 19.5 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710
| 20 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710
| 20.5 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710 | 3710
| 21 | 3689 | 3689 | 3689 | 3689 | 3689 | 3689 | 3689 | 3689 | 3689 | 3689 | 3689 | 3689 | 3689 | 3689 | 3689 | 3689 | 3689
| 21.5 | 3537 | 3537 | 3537 | 3537 | 3537 | 3537 | 3537 | 3537 | 3537 | 3537 | 3537 | 3537 | 3537 | 3537 | 3537 | 3537 | 3537
| 22 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327
| 22.5 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003
| 23 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906
| 23.5 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874
| 24 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855
| 24.5 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835
| 25 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.62639 | 0.62639 | 0.62639 | 0.62639 | 0.62708 | 0.62778 | 0.62847 | 0.62917 | 0.62986 | 0.63056 | 0.63125 | 0.63194 | 0.63194 | 0.63264 | 0.63333 | 0.63403 | 0.63403
| 3.5 | 0.62083 | 0.62153 | 0.62222 | 0.62292 | 0.62361 | 0.62361 | 0.62431 | 0.625 | 0.625 | 0.62569 | 0.62569 | 0.62639 | 0.62639 | 0.62708 | 0.62708 | 0.62778 | 0.62778
| 4 | 0.61597 | 0.61667 | 0.61667 | 0.61667 | 0.61736 | 0.61736 | 0.61736 | 0.61806 | 0.61806 | 0.61875 | 0.61875 | 0.61875 | 0.61944 | 0.61944 | 0.61944 | 0.61944 | 0.61944
| 4.5 | 0.61111 | 0.61111 | 0.61111 | 0.61111 | 0.61111 | 0.61111 | 0.61111 | 0.61111 | 0.61181 | 0.61181 | 0.61181 | 0.61181 | 0.61181 | 0.61181 | 0.61181 | 0.61181 | 0.61181
| 5 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60486 | 0.60486 | 0.60486 | 0.60486 | 0.60486
| 5.5 | 0.6 | 0.59931 | 0.59931 | 0.59931 | 0.59861 | 0.59861 | 0.59861 | 0.59861 | 0.59861 | 0.59792 | 0.59792 | 0.59792 | 0.59792 | 0.59722 | 0.59722 | 0.59722 | 0.59722
| 6 | 0.59583 | 0.59514 | 0.59514 | 0.59514 | 0.59444 | 0.59444 | 0.59444 | 0.59375 | 0.59375 | 0.59375 | 0.59375 | 0.59306 | 0.59306 | 0.59306 | 0.59306 | 0.59236 | 0.59236
| 6.5 | 0.59375 | 0.59306 | 0.59306 | 0.59306 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59167 | 0.59167 | 0.59167 | 0.59167 | 0.59167 | 0.59097 | 0.59097 | 0.59097 | 0.59097
| 7 | 0.59167 | 0.59167 | 0.59167 | 0.59097 | 0.59097 | 0.59097 | 0.59097 | 0.59028 | 0.59028 | 0.59028 | 0.59028 | 0.59028 | 0.59028 | 0.58958 | 0.58958 | 0.58958 | 0.58958
| 7.5 | 0.59028 | 0.59028 | 0.59028 | 0.59028 | 0.58958 | 0.58958 | 0.58958 | 0.58958 | 0.58889 | 0.58889 | 0.58889 | 0.58889 | 0.58889 | 0.58889 | 0.58889 | 0.58819 | 0.58819
| 8 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.5875 | 0.5875 | 0.5875 | 0.5875 | 0.5875 | 0.5875 | 0.5875
| 8.5 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944
| 9 | 0.54444 | 0.54444 | 0.54444 | 0.54444 | 0.54444 | 0.54444 | 0.54444 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54306 | 0.54306 | 0.54306 | 0.54236 | 0.54236 | 0.54236
| 9.5 | 0.51528 | 0.51528 | 0.51458 | 0.51458 | 0.51389 | 0.51389 | 0.51319 | 0.5125 | 0.5125 | 0.51181 | 0.51111 | 0.51042 | 0.50972 | 0.50903 | 0.50833 | 0.50764 | 0.50694
| 10 | 0.4875 | 0.48681 | 0.48611 | 0.48542 | 0.48542 | 0.48472 | 0.48403 | 0.48333 | 0.48264 | 0.48194 | 0.48056 | 0.47986 | 0.47917 | 0.47778 | 0.47708 | 0.47569 | 0.45903
| 10.5 | 0.46111 | 0.46042 | 0.45972 | 0.45903 | 0.45833 | 0.45764 | 0.45694 | 0.45556 | 0.45486 | 0.45417 | 0.43958 | 0.42361 | 0.40972 | 0.39722 | 0.38611 | 0.37569 | 0.36597
| 11 | 0.43611 | 0.43611 | 0.43472 | 0.43403 | 0.43333 | 0.42222 | 0.40625 | 0.39167 | 0.37917 | 0.36736 | 0.35694 | 0.34653 | 0.3375 | 0.32917 | 0.32083 | 0.31319 | 0.30625
| 11.5 | 0.41319 | 0.40278 | 0.38681 | 0.37222 | 0.35972 | 0.34792 | 0.33681 | 0.32708 | 0.31806 | 0.30903 | 0.30139 | 0.29375 | 0.28611 | 0.27986 | 0.27361 | 0.26736 | 0.26181
| 12 | 0.34861 | 0.33611 | 0.325 | 0.31458 | 0.30486 | 0.29583 | 0.2875 | 0.27986 | 0.27222 | 0.26528 | 0.25903 | 0.25278 | 0.24722 | 0.24167 | 0.23611 | 0.23125 | 0.22639
| 12.5 | 0.29792 | 0.28819 | 0.27986 | 0.27153 | 0.26389 | 0.25625 | 0.24931 | 0.24306 | 0.23681 | 0.23125 | 0.22569 | 0.22083 | 0.21597 | 0.21111 | 0.20694 | 0.20278 | 0.19861
| 13 | 0.25972 | 0.25139 | 0.24375 | 0.2375 | 0.23056 | 0.22431 | 0.21875 | 0.21319 | 0.20833 | 0.20347 | 0.19861 | 0.19444 | 0.19028 | 0.18611 | 0.18264 | 0.17917 | 0.175
| 13.5 | 0.22847 | 0.22153 | 0.21528 | 0.20903 | 0.20347 | 0.19861 | 0.19375 | 0.18889 | 0.18472 | 0.18056 | 0.17639 | 0.17222 | 0.16875 | 0.16528 | 0.1625 | 0.15903 | 0.15625
| 14 | 0.20278 | 0.19653 | 0.19097 | 0.18611 | 0.18125 | 0.17708 | 0.17222 | 0.16875 | 0.16458 | 0.16111 | 0.15764 | 0.15417 | 0.15069 | 0.14792 | 0.14514 | 0.14236 | 0.13958
| 14.5 | 0.18056 | 0.17569 | 0.17083 | 0.16667 | 0.1625 | 0.15833 | 0.15486 | 0.15139 | 0.14792 | 0.14444 | 0.14167 | 0.13819 | 0.13542 | 0.13333 | 0.13056 | 0.12778 | 0.12569
| 15 | 0.1625 | 0.15833 | 0.15417 | 0.15 | 0.14653 | 0.14306 | 0.13958 | 0.13611 | 0.13333 | 0.13056 | 0.12778 | 0.125 | 0.12222 | 0.12014 | 0.11806 | 0.11597 | 0.11389
| 15.5 | 0.14722 | 0.14306 | 0.13958 | 0.13611 | 0.13264 | 0.12917 | 0.12639 | 0.12361 | 0.12083 | 0.11806 | 0.11597 | 0.11319 | 0.11111 | 0.10903 | 0.10694 | 0.10486 | 0.10347
| 16 | 0.13333 | 0.12986 | 0.12639 | 0.12361 | 0.12083 | 0.11736 | 0.11528 | 0.1125 | 0.10972 | 0.10764 | 0.10556 | 0.10347 | 0.10139 | 0.099306 | 0.097917 | 0.095833 | 0.094444
| 16.5 | 0.12153 | 0.11875 | 0.11528 | 0.1125 | 0.10972 | 0.10764 | 0.10486 | 0.10278 | 0.10069 | 0.098611 | 0.096528 | 0.094444 | 0.093056 | 0.090972 | 0.089583 | 0.0875 | 0.086111
| 17 | 0.11111 | 0.10833 | 0.10556 | 0.10347 | 0.10069 | 0.098611 | 0.096528 | 0.094444 | 0.092361 | 0.090278 | 0.088889 | 0.086806 | 0.085417 | 0.083333 | 0.081944 | 0.080556 | 0.079167
| 17.5 | 0.10208 | 0.1 | 0.097222 | 0.095139 | 0.092361 | 0.090278 | 0.088889 | 0.086806 | 0.084722 | 0.083333 | 0.081944 | 0.079861 | 0.078472 | 0.077083 | 0.075694 | 0.074306 | 0.072917
| 18 | 0.094444 | 0.091667 | 0.089583 | 0.0875 | 0.085417 | 0.083333 | 0.081944 | 0.079861 | 0.078472 | 0.077083 | 0.075 | 0.073611 | 0.072222 | 0.071528 | 0.070139 | 0.099 | 0.097
| 18.5 | 0.086806 | 0.084722 | 0.082639 | 0.080556 | 0.079167 | 0.077083 | 0.075694 | 0.074306 | 0.072917 | 0.070833 | 0.069444 | 0.099 | 0.097 | 0.095 | 0.094 | 0.092 | 0.09
| 19 | 0.080556 | 0.078472 | 0.077083 | 0.075 | 0.073611 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.092 | 0.09 | 0.088 | 0.087 | 0.085 | 0.084
| 19.5 | 0.075 | 0.072917 | 0.071528 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.089 | 0.087 | 0.085 | 0.084 | 0.082 | 0.081 | 0.08 | 0.078
| 20 | 0.070139 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.086 | 0.084 | 0.083 | 0.081 | 0.08 | 0.078 | 0.077 | 0.076 | 0.074 | 0.073
| 20.5 | 0.093 | 0.091 | 0.089 | 0.087 | 0.085 | 0.083 | 0.081 | 0.08 | 0.078 | 0.077 | 0.075 | 0.074 | 0.072 | 0.071 | 0.07 | 0.068 | 0.068
| 21 | 0.085 | 0.083 | 0.081 | 0.079 | 0.078 | 0.076 | 0.074 | 0.073 | 0.071 | 0.07 | 0.068 | 0.068 | 0.066 | 0.065 | 0.064 | 0.062 | 0.062
| 21.5 | 0.076 | 0.074 | 0.072 | 0.071 | 0.069 | 0.068 | 0.066 | 0.065 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055
| 22 | 0.066 | 0.064 | 0.063 | 0.062 | 0.06 | 0.059 | 0.058 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.051 | 0.05 | 0.049 | 0.048
| 22.5 | 0.057 | 0.055 | 0.054 | 0.053 | 0.052 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.045 | 0.044 | 0.043 | 0.043 | 0.041 | 0.041
| 23 | 0.052 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.041 | 0.04 | 0.039 | 0.039 | 0.038 | 0.037
| 23.5 | 0.049 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036 | 0.035
| 24 | 0.046 | 0.044 | 0.043 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.034 | 0.033
| 24.5 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.033 | 0.032 | 0.031 | 0.031
| 25 | 0.04 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.032 | 0.031 | 0.03 | 0.03 | 0.029 | 0.029