## Sheet1
PROPERTIES
General
Name | Nordex N131/3.9 Mode 3 3,6MW
Manufacturer | Nordex
Hub Height | 84 | 114 | 120 | 134 | 164
Power
Rated Power | 3600
Peak Power | 3600
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 131
Number of blades | 3
Rated RPM | 12.6
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 25
Restart Wind Speed | 19.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 40
High Temperature Restart | 38
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | III
Turbine SubClass | S
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 40
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 1 | 3 | 4 | 5 | 7 | 8 | 9 | 10 | 12 | 13 | 14 | 15 | 17 | 18 | 19 | 21 | 22
| 3.5 | 52 | 55 | 58 | 61 | 63 | 66 | 69 | 71 | 74 | 77 | 79 | 82 | 85 | 87 | 90 | 93 | 95
| 4 | 122 | 127 | 132 | 136 | 141 | 146 | 150 | 155 | 159 | 164 | 169 | 173 | 178 | 182 | 187 | 192 | 196
| 4.5 | 210 | 218 | 225 | 232 | 239 | 246 | 253 | 260 | 267 | 274 | 281 | 288 | 295 | 302 | 309 | 316 | 323
| 5 | 317 | 327 | 337 | 347 | 357 | 367 | 377 | 387 | 397 | 407 | 417 | 427 | 437 | 447 | 457 | 467 | 477
| 5.5 | 442 | 456 | 469 | 483 | 496 | 510 | 523 | 537 | 550 | 563 | 577 | 590 | 604 | 617 | 630 | 644 | 657
| 6 | 589 | 607 | 624 | 642 | 659 | 676 | 694 | 711 | 729 | 746 | 764 | 781 | 798 | 816 | 833 | 851 | 868
| 6.5 | 760 | 782 | 805 | 827 | 849 | 871 | 893 | 915 | 937 | 959 | 981 | 1003 | 1025 | 1047 | 1069 | 1091 | 1113
| 7 | 958 | 986 | 1013 | 1041 | 1068 | 1096 | 1123 | 1150 | 1178 | 1205 | 1232 | 1260 | 1287 | 1314 | 1341 | 1369 | 1396
| 7.5 | 1186 | 1219 | 1253 | 1286 | 1320 | 1353 | 1387 | 1420 | 1454 | 1487 | 1520 | 1553 | 1587 | 1620 | 1653 | 1686 | 1719
| 8 | 1444 | 1484 | 1525 | 1565 | 1606 | 1646 | 1686 | 1726 | 1766 | 1806 | 1847 | 1887 | 1927 | 1967 | 2006 | 2046 | 2085
| 8.5 | 1730 | 1778 | 1825 | 1873 | 1921 | 1969 | 2016 | 2064 | 2111 | 2158 | 2205 | 2252 | 2299 | 2345 | 2393 | 2440 | 2487
| 9 | 2035 | 2091 | 2146 | 2202 | 2257 | 2312 | 2367 | 2421 | 2476 | 2531 | 2586 | 2641 | 2696 | 2750 | 2798 | 2842 | 2886
| 9.5 | 2353 | 2417 | 2480 | 2543 | 2606 | 2669 | 2731 | 2794 | 2852 | 2901 | 2950 | 2999 | 3047 | 3096 | 3134 | 3167 | 3200
| 10 | 2678 | 2749 | 2819 | 2889 | 2945 | 2999 | 3053 | 3107 | 3156 | 3193 | 3231 | 3268 | 3304 | 3341 | 3369 | 3392 | 3415
| 10.5 | 2988 | 3047 | 3107 | 3166 | 3210 | 3251 | 3293 | 3334 | 3371 | 3397 | 3423 | 3449 | 3475 | 3500 | 3518 | 3530 | 3542
| 11 | 3228 | 3274 | 3320 | 3366 | 3398 | 3427 | 3457 | 3486 | 3511 | 3526 | 3541 | 3555 | 3570 | 3584 | 3591 | 3593 | 3594
| 11.5 | 3402 | 3435 | 3468 | 3501 | 3520 | 3538 | 3556 | 3573 | 3586 | 3589 | 3592 | 3595 | 3598 | 3600 | 3600 | 3600 | 3600
| 12 | 3517 | 3538 | 3558 | 3579 | 3585 | 3590 | 3595 | 3599 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 12.5 | 3581 | 3588 | 3595 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 13 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 13.5 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 14 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 14.5 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 15 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 15.5 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 16 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 16.5 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 17 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 17.5 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 18 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 18.5 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 19 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 19.5 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 20 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 20.5 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 21 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 21.5 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500
| 22 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327
| 22.5 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003
| 23 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906
| 23.5 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874
| 24 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855
| 24.5 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835
| 25 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.62639 | 0.62639 | 0.62639 | 0.62639 | 0.62708 | 0.62778 | 0.62847 | 0.62917 | 0.62986 | 0.63056 | 0.63125 | 0.63125 | 0.63194 | 0.63264 | 0.63333 | 0.63403 | 0.63403
| 3.5 | 0.62083 | 0.62153 | 0.62222 | 0.62292 | 0.62361 | 0.62361 | 0.62431 | 0.625 | 0.625 | 0.62569 | 0.62569 | 0.62639 | 0.62639 | 0.62708 | 0.62708 | 0.62778 | 0.62778
| 4 | 0.61597 | 0.61667 | 0.61667 | 0.61736 | 0.61736 | 0.61736 | 0.61806 | 0.61806 | 0.61806 | 0.61875 | 0.61875 | 0.61875 | 0.61944 | 0.61944 | 0.61944 | 0.61944 | 0.62014
| 4.5 | 0.61111 | 0.61111 | 0.61111 | 0.61111 | 0.61111 | 0.61181 | 0.61181 | 0.61181 | 0.61181 | 0.61181 | 0.61181 | 0.61181 | 0.61181 | 0.61181 | 0.6125 | 0.6125 | 0.6125
| 5 | 0.60625 | 0.60625 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556
| 5.5 | 0.6 | 0.6 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59861 | 0.59861 | 0.59861 | 0.59861 | 0.59792 | 0.59792 | 0.59792 | 0.59792 | 0.59792 | 0.59792 | 0.59722
| 6 | 0.59583 | 0.59583 | 0.59583 | 0.59514 | 0.59514 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59375 | 0.59375 | 0.59375 | 0.59306 | 0.59306 | 0.59306 | 0.59306 | 0.59306
| 6.5 | 0.59375 | 0.59375 | 0.59306 | 0.59306 | 0.59306 | 0.59306 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59167 | 0.59167 | 0.59167 | 0.59167 | 0.59167 | 0.59097 | 0.59097
| 7 | 0.59236 | 0.59167 | 0.59167 | 0.59167 | 0.59167 | 0.59097 | 0.59097 | 0.59097 | 0.59097 | 0.59097 | 0.59028 | 0.59028 | 0.59028 | 0.59028 | 0.59028 | 0.59028 | 0.58958
| 7.5 | 0.59097 | 0.59028 | 0.59028 | 0.59028 | 0.59028 | 0.59028 | 0.58958 | 0.58958 | 0.58958 | 0.58958 | 0.58958 | 0.58889 | 0.58889 | 0.58889 | 0.58889 | 0.58889 | 0.58889
| 8 | 0.58889 | 0.58889 | 0.58889 | 0.58889 | 0.58889 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.5875 | 0.5875 | 0.5875
| 8.5 | 0.57569 | 0.57569 | 0.575 | 0.575 | 0.575 | 0.575 | 0.575 | 0.575 | 0.575 | 0.575 | 0.575 | 0.575 | 0.575 | 0.575 | 0.57431 | 0.57431 | 0.57431
| 9 | 0.54792 | 0.54792 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54653 | 0.54653 | 0.54653 | 0.54583 | 0.54583 | 0.54583 | 0.54514 | 0.54514 | 0.54444 | 0.54444 | 0.54375
| 9.5 | 0.51736 | 0.51736 | 0.51667 | 0.51667 | 0.51597 | 0.51528 | 0.51528 | 0.51458 | 0.51389 | 0.51319 | 0.5125 | 0.5125 | 0.51111 | 0.51042 | 0.50972 | 0.50903 | 0.50833
| 10 | 0.48889 | 0.48819 | 0.4875 | 0.4875 | 0.48681 | 0.48611 | 0.48542 | 0.48472 | 0.48333 | 0.48264 | 0.48194 | 0.48125 | 0.47986 | 0.47917 | 0.46597 | 0.44861 | 0.43403
| 10.5 | 0.46181 | 0.46111 | 0.46042 | 0.45972 | 0.45903 | 0.45833 | 0.45764 | 0.45625 | 0.45069 | 0.43264 | 0.41736 | 0.40347 | 0.39097 | 0.37986 | 0.36944 | 0.35972 | 0.35069
| 11 | 0.43681 | 0.43611 | 0.43542 | 0.43472 | 0.41806 | 0.40139 | 0.3875 | 0.37431 | 0.3625 | 0.35208 | 0.34167 | 0.33264 | 0.32431 | 0.31597 | 0.30833 | 0.30139 | 0.29444
| 11.5 | 0.40069 | 0.38403 | 0.36944 | 0.35625 | 0.34444 | 0.33333 | 0.32361 | 0.31389 | 0.30556 | 0.29722 | 0.28958 | 0.28264 | 0.27569 | 0.26944 | 0.26319 | 0.25764 | 0.25208
| 12 | 0.33472 | 0.32292 | 0.3125 | 0.30278 | 0.29306 | 0.28472 | 0.27708 | 0.26944 | 0.2625 | 0.25625 | 0.25 | 0.24444 | 0.23889 | 0.23333 | 0.22847 | 0.22361 | 0.21875
| 12.5 | 0.28681 | 0.27778 | 0.26944 | 0.26181 | 0.25417 | 0.24722 | 0.24097 | 0.23472 | 0.22847 | 0.22361 | 0.21806 | 0.21319 | 0.20833 | 0.20417 | 0.2 | 0.19583 | 0.19167
| 13 | 0.25 | 0.24236 | 0.23542 | 0.22917 | 0.22292 | 0.21667 | 0.21111 | 0.20625 | 0.20139 | 0.19653 | 0.19236 | 0.18819 | 0.18403 | 0.17986 | 0.17639 | 0.17292 | 0.16944
| 13.5 | 0.22014 | 0.21389 | 0.20764 | 0.20208 | 0.19722 | 0.19167 | 0.1875 | 0.18264 | 0.17847 | 0.17431 | 0.17083 | 0.16667 | 0.16319 | 0.16042 | 0.15694 | 0.15417 | 0.15139
| 14 | 0.19583 | 0.19028 | 0.18472 | 0.17986 | 0.17569 | 0.17083 | 0.16667 | 0.16319 | 0.15903 | 0.15556 | 0.15278 | 0.14931 | 0.14583 | 0.14306 | 0.14028 | 0.1375 | 0.13542
| 14.5 | 0.175 | 0.17014 | 0.16528 | 0.16111 | 0.15694 | 0.15347 | 0.15 | 0.14653 | 0.14306 | 0.14028 | 0.13681 | 0.13403 | 0.13125 | 0.12917 | 0.12639 | 0.12431 | 0.12153
| 15 | 0.15764 | 0.15278 | 0.14931 | 0.14514 | 0.14167 | 0.13819 | 0.13542 | 0.13194 | 0.12917 | 0.12639 | 0.12361 | 0.12153 | 0.11875 | 0.11667 | 0.11458 | 0.1125 | 0.11042
| 15.5 | 0.14236 | 0.13889 | 0.13472 | 0.13194 | 0.12847 | 0.125 | 0.12222 | 0.11944 | 0.11736 | 0.11458 | 0.1125 | 0.10972 | 0.10764 | 0.10556 | 0.10417 | 0.10208 | 0.1
| 16 | 0.12917 | 0.12569 | 0.12292 | 0.11944 | 0.11667 | 0.11389 | 0.11111 | 0.10903 | 0.10694 | 0.10417 | 0.10208 | 0.1 | 0.098611 | 0.096528 | 0.094444 | 0.093056 | 0.091667
| 16.5 | 0.11806 | 0.11458 | 0.11181 | 0.10903 | 0.10694 | 0.10417 | 0.10208 | 0.1 | 0.097222 | 0.095833 | 0.09375 | 0.091667 | 0.090278 | 0.088194 | 0.086806 | 0.085417 | 0.084028
| 17 | 0.10833 | 0.10556 | 0.10278 | 0.1 | 0.097917 | 0.095833 | 0.093056 | 0.091667 | 0.089583 | 0.0875 | 0.086111 | 0.084028 | 0.082639 | 0.08125 | 0.079861 | 0.078472 | 0.077083
| 17.5 | 0.099306 | 0.096528 | 0.094444 | 0.091667 | 0.090278 | 0.088194 | 0.086111 | 0.084028 | 0.082639 | 0.080556 | 0.079167 | 0.077778 | 0.076389 | 0.075 | 0.073611 | 0.072222 | 0.070833
| 18 | 0.091667 | 0.088889 | 0.086806 | 0.084722 | 0.083333 | 0.08125 | 0.079167 | 0.077778 | 0.076389 | 0.074306 | 0.072917 | 0.071528 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.095
| 18.5 | 0.084722 | 0.082639 | 0.080556 | 0.078472 | 0.076389 | 0.075 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092 | 0.091 | 0.089 | 0.088
| 19 | 0.078472 | 0.076389 | 0.074306 | 0.072917 | 0.071528 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084 | 0.083 | 0.082
| 19.5 | 0.072917 | 0.070833 | 0.069444 | 0.098 | 0.095 | 0.093 | 0.091 | 0.09 | 0.088 | 0.086 | 0.084 | 0.083 | 0.082 | 0.08 | 0.079 | 0.077 | 0.076
| 20 | 0.098 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.085 | 0.084 | 0.082 | 0.08 | 0.079 | 0.078 | 0.076 | 0.075 | 0.074 | 0.072 | 0.071
| 20.5 | 0.091 | 0.088 | 0.086 | 0.084 | 0.082 | 0.08 | 0.079 | 0.078 | 0.076 | 0.074 | 0.073 | 0.072 | 0.07 | 0.069 | 0.068 | 0.067 | 0.066
| 21 | 0.083 | 0.08 | 0.078 | 0.077 | 0.075 | 0.073 | 0.072 | 0.071 | 0.069 | 0.068 | 0.067 | 0.066 | 0.064 | 0.063 | 0.062 | 0.061 | 0.06
| 21.5 | 0.074 | 0.072 | 0.07 | 0.069 | 0.067 | 0.066 | 0.064 | 0.063 | 0.062 | 0.06 | 0.059 | 0.059 | 0.057 | 0.056 | 0.056 | 0.054 | 0.053
| 22 | 0.064 | 0.062 | 0.061 | 0.06 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.052 | 0.052 | 0.051 | 0.05 | 0.049 | 0.049 | 0.047 | 0.047
| 22.5 | 0.055 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04
| 23 | 0.05 | 0.049 | 0.048 | 0.047 | 0.045 | 0.044 | 0.043 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037 | 0.036
| 23.5 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034
| 24 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.034 | 0.034 | 0.033 | 0.032
| 24.5 | 0.042 | 0.04 | 0.039 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.032 | 0.031 | 0.031 | 0.03
| 25 | 0.039 | 0.038 | 0.037 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032 | 0.032 | 0.031 | 0.031 | 0.03 | 0.03 | 0.029 | 0.028 | 0.028