## Sheet1
PROPERTIES
General
Name | Nordex N131/3.9 Mode 5 3,4MW
Manufacturer | Nordex
Hub Height | 84 | 120 | 134 | 164
Power
Rated Power | 3400
Peak Power | 3400
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 131
Number of blades | 3
Rated RPM | 12.6
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 25
Restart Wind Speed | 19.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 40
High Temperature Restart | 38
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | III
Turbine SubClass | S
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 40
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 1 | 3 | 4 | 5 | 7 | 8 | 9 | 10 | 12 | 13 | 14 | 15 | 17 | 18 | 19 | 21 | 22
| 3.5 | 52 | 55 | 58 | 61 | 63 | 66 | 69 | 71 | 74 | 77 | 79 | 82 | 85 | 87 | 90 | 93 | 95
| 4 | 122 | 127 | 132 | 136 | 141 | 146 | 150 | 155 | 159 | 164 | 169 | 173 | 178 | 182 | 187 | 192 | 196
| 4.5 | 210 | 217 | 225 | 232 | 239 | 246 | 253 | 260 | 267 | 274 | 281 | 288 | 295 | 302 | 309 | 316 | 323
| 5 | 317 | 327 | 337 | 347 | 357 | 367 | 377 | 387 | 397 | 407 | 417 | 427 | 437 | 447 | 457 | 467 | 477
| 5.5 | 442 | 456 | 469 | 483 | 496 | 510 | 523 | 536 | 550 | 563 | 577 | 590 | 604 | 617 | 630 | 644 | 657
| 6 | 589 | 607 | 624 | 641 | 659 | 676 | 694 | 711 | 729 | 746 | 764 | 781 | 798 | 816 | 833 | 850 | 868
| 6.5 | 760 | 782 | 804 | 827 | 849 | 871 | 893 | 915 | 937 | 959 | 981 | 1003 | 1025 | 1047 | 1069 | 1091 | 1113
| 7 | 958 | 986 | 1013 | 1041 | 1068 | 1095 | 1123 | 1150 | 1177 | 1205 | 1232 | 1259 | 1287 | 1314 | 1341 | 1368 | 1395
| 7.5 | 1186 | 1219 | 1253 | 1286 | 1320 | 1353 | 1387 | 1420 | 1453 | 1487 | 1520 | 1553 | 1587 | 1620 | 1653 | 1686 | 1719
| 8 | 1444 | 1484 | 1524 | 1565 | 1605 | 1645 | 1686 | 1726 | 1766 | 1806 | 1846 | 1886 | 1926 | 1965 | 2005 | 2044 | 2084
| 8.5 | 1726 | 1774 | 1822 | 1870 | 1918 | 1965 | 2013 | 2060 | 2107 | 2154 | 2201 | 2248 | 2296 | 2343 | 2391 | 2439 | 2486
| 9 | 2027 | 2083 | 2138 | 2193 | 2248 | 2303 | 2359 | 2414 | 2470 | 2525 | 2581 | 2631 | 2676 | 2720 | 2764 | 2808 | 2853
| 9.5 | 2338 | 2402 | 2465 | 2528 | 2592 | 2655 | 2711 | 2760 | 2810 | 2859 | 2909 | 2951 | 2985 | 3018 | 3051 | 3084 | 3117
| 10 | 2653 | 2724 | 2783 | 2838 | 2893 | 2948 | 2993 | 3030 | 3068 | 3106 | 3143 | 3175 | 3198 | 3221 | 3244 | 3267 | 3290
| 10.5 | 2924 | 2984 | 3032 | 3074 | 3116 | 3158 | 3192 | 3218 | 3245 | 3271 | 3298 | 3318 | 3331 | 3343 | 3355 | 3368 | 3380
| 11 | 3127 | 3174 | 3209 | 3239 | 3269 | 3299 | 3321 | 3336 | 3351 | 3366 | 3381 | 3391 | 3393 | 3394 | 3396 | 3398 | 3400
| 11.5 | 3268 | 3302 | 3324 | 3342 | 3360 | 3378 | 3388 | 3391 | 3394 | 3397 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400
| 12 | 3355 | 3376 | 3386 | 3391 | 3396 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400
| 12.5 | 3393 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400
| 13 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400
| 13.5 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400
| 14 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400
| 14.5 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400
| 15 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400
| 15.5 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400
| 16 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400
| 16.5 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400
| 17 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400
| 17.5 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400
| 18 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400
| 18.5 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400
| 19 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400
| 19.5 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400
| 20 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400
| 20.5 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400
| 21 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400
| 21.5 | 3369 | 3369 | 3369 | 3369 | 3369 | 3369 | 3369 | 3369 | 3369 | 3369 | 3369 | 3369 | 3369 | 3369 | 3369 | 3369 | 3369
| 22 | 3242 | 3242 | 3242 | 3242 | 3242 | 3242 | 3242 | 3242 | 3242 | 3242 | 3242 | 3242 | 3242 | 3242 | 3242 | 3242 | 3242
| 22.5 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003 | 3003
| 23 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906 | 2906
| 23.5 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874
| 24 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855
| 24.5 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835
| 25 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.62639 | 0.62639 | 0.62639 | 0.62639 | 0.62708 | 0.62778 | 0.62847 | 0.62917 | 0.62986 | 0.63056 | 0.63125 | 0.63194 | 0.63194 | 0.63264 | 0.63333 | 0.63333 | 0.63403
| 3.5 | 0.62083 | 0.62153 | 0.62222 | 0.62292 | 0.62361 | 0.62361 | 0.62431 | 0.625 | 0.625 | 0.62569 | 0.62639 | 0.62639 | 0.62708 | 0.62708 | 0.62778 | 0.62778 | 0.62778
| 4 | 0.61667 | 0.61667 | 0.61667 | 0.61736 | 0.61736 | 0.61806 | 0.61806 | 0.61806 | 0.61875 | 0.61875 | 0.61944 | 0.61944 | 0.61944 | 0.61944 | 0.61944 | 0.62014 | 0.62014
| 4.5 | 0.61111 | 0.61111 | 0.61181 | 0.61181 | 0.61181 | 0.61181 | 0.61181 | 0.61181 | 0.61181 | 0.6125 | 0.6125 | 0.6125 | 0.6125 | 0.6125 | 0.6125 | 0.6125 | 0.6125
| 5 | 0.60625 | 0.60625 | 0.60625 | 0.60625 | 0.60625 | 0.60625 | 0.60625 | 0.60625 | 0.60625 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556 | 0.60556
| 5.5 | 0.60069 | 0.6 | 0.6 | 0.6 | 0.6 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59861 | 0.59861 | 0.59861 | 0.59861 | 0.59861 | 0.59792 | 0.59792 | 0.59792
| 6 | 0.59653 | 0.59653 | 0.59583 | 0.59583 | 0.59583 | 0.59514 | 0.59514 | 0.59514 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59375 | 0.59375 | 0.59375 | 0.59375 | 0.59306
| 6.5 | 0.59444 | 0.59444 | 0.59375 | 0.59375 | 0.59375 | 0.59306 | 0.59306 | 0.59306 | 0.59306 | 0.59306 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59167 | 0.59167
| 7 | 0.59306 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59167 | 0.59167 | 0.59167 | 0.59167 | 0.59167 | 0.59097 | 0.59097 | 0.59097 | 0.59097 | 0.59097 | 0.59097 | 0.59028
| 7.5 | 0.59167 | 0.59167 | 0.59097 | 0.59097 | 0.59097 | 0.59097 | 0.59028 | 0.59028 | 0.59028 | 0.59028 | 0.59028 | 0.59028 | 0.59028 | 0.58958 | 0.58958 | 0.58958 | 0.58958
| 8 | 0.58958 | 0.58958 | 0.58958 | 0.58889 | 0.58889 | 0.58889 | 0.58889 | 0.58889 | 0.58889 | 0.58889 | 0.58889 | 0.58889 | 0.58889 | 0.58889 | 0.58819 | 0.58819 | 0.58819
| 8.5 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56806 | 0.56806 | 0.56806 | 0.56806 | 0.56806 | 0.56806 | 0.56806 | 0.56806 | 0.56806 | 0.56806 | 0.56806
| 9 | 0.53819 | 0.5375 | 0.5375 | 0.5375 | 0.5375 | 0.5375 | 0.5375 | 0.53681 | 0.53681 | 0.53681 | 0.53611 | 0.53611 | 0.53611 | 0.53542 | 0.53542 | 0.53472 | 0.53472
| 9.5 | 0.50833 | 0.50833 | 0.50833 | 0.50833 | 0.50764 | 0.50764 | 0.50694 | 0.50694 | 0.50694 | 0.50625 | 0.50625 | 0.50556 | 0.50556 | 0.50486 | 0.50417 | 0.50417 | 0.50417
| 10 | 0.48056 | 0.48056 | 0.48056 | 0.47986 | 0.47986 | 0.47917 | 0.47917 | 0.47847 | 0.47847 | 0.47847 | 0.47847 | 0.46944 | 0.45 | 0.43403 | 0.41944 | 0.40694 | 0.39514
| 10.5 | 0.45417 | 0.45347 | 0.45347 | 0.45278 | 0.45278 | 0.45278 | 0.44097 | 0.42292 | 0.40764 | 0.39375 | 0.38125 | 0.37014 | 0.35972 | 0.35 | 0.34097 | 0.33194 | 0.32431
| 11 | 0.42847 | 0.42847 | 0.41389 | 0.39653 | 0.38194 | 0.36806 | 0.35625 | 0.34514 | 0.33472 | 0.32569 | 0.31667 | 0.30833 | 0.30069 | 0.29375 | 0.28681 | 0.28056 | 0.27431
| 11.5 | 0.36736 | 0.35347 | 0.34097 | 0.32917 | 0.31875 | 0.30903 | 0.3 | 0.29167 | 0.28403 | 0.27708 | 0.27014 | 0.26319 | 0.25694 | 0.25139 | 0.24583 | 0.24028 | 0.23542
| 12 | 0.31042 | 0.3 | 0.29028 | 0.28125 | 0.27292 | 0.26528 | 0.25833 | 0.25139 | 0.24514 | 0.23889 | 0.23333 | 0.22778 | 0.22292 | 0.21806 | 0.21319 | 0.20903 | 0.20486
| 12.5 | 0.26736 | 0.25903 | 0.25139 | 0.24444 | 0.2375 | 0.23125 | 0.225 | 0.21944 | 0.21389 | 0.20903 | 0.20417 | 0.19931 | 0.19514 | 0.19097 | 0.1875 | 0.18333 | 0.17986
| 13 | 0.23333 | 0.22639 | 0.22014 | 0.21389 | 0.20833 | 0.20278 | 0.19792 | 0.19306 | 0.18889 | 0.18403 | 0.17986 | 0.17639 | 0.17222 | 0.16875 | 0.16528 | 0.1625 | 0.15903
| 13.5 | 0.20625 | 0.2 | 0.19444 | 0.18958 | 0.18472 | 0.17986 | 0.17569 | 0.17153 | 0.16736 | 0.16389 | 0.15972 | 0.15694 | 0.15347 | 0.15 | 0.14722 | 0.14444 | 0.14167
| 14 | 0.18333 | 0.17847 | 0.17361 | 0.16875 | 0.16458 | 0.16042 | 0.15694 | 0.15278 | 0.14931 | 0.14653 | 0.14306 | 0.14028 | 0.1375 | 0.13472 | 0.13194 | 0.12917 | 0.12708
| 14.5 | 0.16389 | 0.15972 | 0.15556 | 0.15139 | 0.14792 | 0.14444 | 0.14097 | 0.1375 | 0.13472 | 0.13125 | 0.12917 | 0.12639 | 0.12361 | 0.12083 | 0.11875 | 0.11667 | 0.11458
| 15 | 0.14792 | 0.14375 | 0.14028 | 0.13681 | 0.13333 | 0.12986 | 0.12708 | 0.12431 | 0.12153 | 0.11875 | 0.11667 | 0.11389 | 0.11181 | 0.10972 | 0.10764 | 0.10556 | 0.10347
| 15.5 | 0.13403 | 0.13056 | 0.12708 | 0.12361 | 0.12083 | 0.11806 | 0.11528 | 0.1125 | 0.11042 | 0.10764 | 0.10556 | 0.10347 | 0.10139 | 0.1 | 0.097917 | 0.095833 | 0.094444
| 16 | 0.12153 | 0.11875 | 0.11528 | 0.1125 | 0.10972 | 0.10764 | 0.10486 | 0.10278 | 0.10069 | 0.098611 | 0.096528 | 0.094444 | 0.093056 | 0.090972 | 0.089583 | 0.0875 | 0.086111
| 16.5 | 0.11111 | 0.10833 | 0.10556 | 0.10278 | 0.10069 | 0.097917 | 0.095833 | 0.09375 | 0.091667 | 0.090278 | 0.088194 | 0.086806 | 0.084722 | 0.083333 | 0.081944 | 0.080556 | 0.079167
| 17 | 0.10139 | 0.099306 | 0.096528 | 0.094444 | 0.092361 | 0.090278 | 0.088194 | 0.086111 | 0.084722 | 0.082639 | 0.08125 | 0.079167 | 0.077778 | 0.076389 | 0.075 | 0.073611 | 0.072917
| 17.5 | 0.09375 | 0.090972 | 0.088889 | 0.086806 | 0.084722 | 0.082639 | 0.08125 | 0.079167 | 0.077778 | 0.076389 | 0.075 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096
| 18 | 0.086111 | 0.084028 | 0.081944 | 0.079861 | 0.078472 | 0.076389 | 0.075 | 0.073611 | 0.071528 | 0.070139 | 0.099 | 0.098 | 0.096 | 0.094 | 0.092 | 0.091 | 0.089
| 18.5 | 0.079861 | 0.077778 | 0.075694 | 0.074306 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.089 | 0.087 | 0.086 | 0.084 | 0.083
| 19 | 0.073611 | 0.072222 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084 | 0.083 | 0.081 | 0.08 | 0.078 | 0.077
| 19.5 | 0.099 | 0.097 | 0.094 | 0.092 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083 | 0.081 | 0.08 | 0.078 | 0.077 | 0.076 | 0.074 | 0.073 | 0.072
| 20 | 0.092 | 0.09 | 0.088 | 0.086 | 0.084 | 0.082 | 0.081 | 0.079 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.071 | 0.07 | 0.068 | 0.067
| 20.5 | 0.085 | 0.083 | 0.081 | 0.08 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.07 | 0.069 | 0.068 | 0.067 | 0.066 | 0.065 | 0.063 | 0.062
| 21 | 0.078 | 0.076 | 0.074 | 0.073 | 0.071 | 0.069 | 0.068 | 0.067 | 0.066 | 0.064 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059 | 0.057 | 0.057
| 21.5 | 0.069 | 0.068 | 0.066 | 0.065 | 0.063 | 0.062 | 0.061 | 0.059 | 0.059 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.053 | 0.051 | 0.05
| 22 | 0.06 | 0.059 | 0.058 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.047 | 0.046 | 0.045 | 0.044
| 22.5 | 0.052 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038 | 0.038
| 23 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034
| 23.5 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032
| 24 | 0.042 | 0.041 | 0.04 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.033 | 0.032 | 0.032 | 0.031 | 0.03
| 24.5 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.032 | 0.031 | 0.031 | 0.03 | 0.03 | 0.029 | 0.028
| 25 | 0.036 | 0.036 | 0.035 | 0.034 | 0.033 | 0.032 | 0.032 | 0.031 | 0.031 | 0.03 | 0.03 | 0.029 | 0.028 | 0.028 | 0.028 | 0.027 | 0.026