## Sheet1
PROPERTIES
General
Name | Nordex N131/3.9 Mode 8 2,92MW
Manufacturer | Nordex
Hub Height | 84 | 114 | 120 | 134 | 164
Power
Rated Power | 2920
Peak Power | 2920
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 131
Number of blades | 3
Rated RPM | 12.6
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 25
Restart Wind Speed | 19.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 40
High Temperature Restart | 38
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | III
Turbine SubClass | S
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 40
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 1 | 3 | 4 | 5 | 7 | 8 | 9 | 10 | 12 | 13 | 14 | 15 | 17 | 18 | 19 | 21 | 22
| 3.5 | 52 | 55 | 58 | 60 | 63 | 66 | 69 | 71 | 74 | 77 | 79 | 82 | 85 | 87 | 90 | 93 | 95
| 4 | 122 | 127 | 132 | 136 | 141 | 145 | 150 | 155 | 159 | 164 | 169 | 173 | 178 | 182 | 187 | 192 | 196
| 4.5 | 210 | 217 | 224 | 232 | 239 | 246 | 253 | 260 | 267 | 274 | 281 | 288 | 295 | 302 | 309 | 316 | 323
| 5 | 317 | 327 | 337 | 347 | 357 | 367 | 377 | 387 | 397 | 407 | 417 | 427 | 437 | 447 | 456 | 466 | 476
| 5.5 | 442 | 456 | 469 | 483 | 496 | 509 | 523 | 536 | 550 | 563 | 577 | 590 | 603 | 617 | 630 | 644 | 657
| 6 | 589 | 606 | 624 | 641 | 659 | 676 | 693 | 711 | 728 | 746 | 763 | 781 | 798 | 815 | 833 | 850 | 867
| 6.5 | 760 | 782 | 804 | 827 | 849 | 871 | 893 | 915 | 937 | 959 | 981 | 1003 | 1025 | 1047 | 1069 | 1091 | 1113
| 7 | 956 | 984 | 1011 | 1039 | 1066 | 1094 | 1121 | 1149 | 1176 | 1204 | 1231 | 1258 | 1286 | 1313 | 1340 | 1368 | 1395
| 7.5 | 1167 | 1200 | 1234 | 1268 | 1301 | 1335 | 1369 | 1403 | 1436 | 1470 | 1504 | 1537 | 1571 | 1604 | 1638 | 1671 | 1705
| 8 | 1384 | 1423 | 1464 | 1504 | 1545 | 1586 | 1627 | 1667 | 1708 | 1748 | 1790 | 1830 | 1870 | 1910 | 1951 | 1991 | 2034
| 8.5 | 1601 | 1646 | 1694 | 1741 | 1789 | 1838 | 1887 | 1934 | 1981 | 2029 | 2079 | 2126 | 2176 | 2223 | 2273 | 2314 | 2356
| 9 | 1815 | 1867 | 1921 | 1976 | 2032 | 2088 | 2144 | 2199 | 2255 | 2310 | 2367 | 2411 | 2457 | 2500 | 2547 | 2580 | 2611
| 9.5 | 2028 | 2086 | 2147 | 2209 | 2272 | 2336 | 2400 | 2452 | 2501 | 2551 | 2600 | 2633 | 2667 | 2700 | 2735 | 2758 | 2780
| 10 | 2238 | 2302 | 2369 | 2438 | 2497 | 2553 | 2608 | 2649 | 2686 | 2724 | 2761 | 2783 | 2807 | 2830 | 2854 | 2867 | 2878
| 10.5 | 2442 | 2509 | 2566 | 2623 | 2671 | 2713 | 2756 | 2785 | 2811 | 2838 | 2863 | 2875 | 2888 | 2900 | 2913 | 2916 | 2917
| 11 | 2615 | 2669 | 2713 | 2757 | 2793 | 2823 | 2853 | 2871 | 2886 | 2901 | 2914 | 2915 | 2917 | 2919 | 2920 | 2920 | 2920
| 11.5 | 2742 | 2785 | 2816 | 2848 | 2871 | 2889 | 2907 | 2913 | 2916 | 2919 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920
| 12 | 2832 | 2862 | 2881 | 2901 | 2911 | 2916 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920
| 12.5 | 2888 | 2906 | 2913 | 2919 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920
| 13 | 2914 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920
| 13.5 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920
| 14 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920
| 14.5 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920
| 15 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920
| 15.5 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920
| 16 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920
| 16.5 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920
| 17 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920
| 17.5 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920
| 18 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920
| 18.5 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920
| 19 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920
| 19.5 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920
| 20 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920
| 20.5 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920
| 21 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920
| 21.5 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920
| 22 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920 | 2920
| 22.5 | 2916 | 2916 | 2916 | 2916 | 2916 | 2916 | 2916 | 2916 | 2916 | 2916 | 2916 | 2916 | 2916 | 2916 | 2916 | 2916 | 2916
| 23 | 2901 | 2901 | 2901 | 2901 | 2901 | 2901 | 2901 | 2901 | 2901 | 2901 | 2901 | 2901 | 2901 | 2901 | 2901 | 2901 | 2901
| 23.5 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874 | 2874
| 24 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855 | 2855
| 24.5 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835
| 25 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.62639 | 0.62639 | 0.62639 | 0.62639 | 0.62708 | 0.62778 | 0.62847 | 0.62917 | 0.62986 | 0.63056 | 0.63125 | 0.63194 | 0.63194 | 0.63264 | 0.63333 | 0.63403 | 0.63472
| 3.5 | 0.62153 | 0.62222 | 0.62292 | 0.62361 | 0.62361 | 0.62431 | 0.625 | 0.625 | 0.62569 | 0.62639 | 0.62639 | 0.62708 | 0.62708 | 0.62778 | 0.62778 | 0.62847 | 0.62847
| 4 | 0.61736 | 0.61736 | 0.61806 | 0.61806 | 0.61806 | 0.61875 | 0.61875 | 0.61944 | 0.61944 | 0.61944 | 0.62014 | 0.62014 | 0.62014 | 0.62014 | 0.62083 | 0.62083 | 0.62083
| 4.5 | 0.6125 | 0.6125 | 0.6125 | 0.6125 | 0.61319 | 0.61319 | 0.61319 | 0.61319 | 0.61319 | 0.61319 | 0.61319 | 0.61319 | 0.61319 | 0.61389 | 0.61389 | 0.61389 | 0.61389
| 5 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60694 | 0.60694 | 0.60694 | 0.60694 | 0.60694 | 0.60694 | 0.60694 | 0.60694 | 0.60694 | 0.60694
| 5.5 | 0.60208 | 0.60208 | 0.60139 | 0.60139 | 0.60139 | 0.60139 | 0.60069 | 0.60069 | 0.60069 | 0.60069 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.59931 | 0.59931
| 6 | 0.59861 | 0.59792 | 0.59792 | 0.59722 | 0.59722 | 0.59722 | 0.59722 | 0.59653 | 0.59653 | 0.59653 | 0.59653 | 0.59583 | 0.59583 | 0.59583 | 0.59583 | 0.59583 | 0.59514
| 6.5 | 0.59653 | 0.59583 | 0.59583 | 0.59583 | 0.59583 | 0.59514 | 0.59514 | 0.59514 | 0.59514 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59375 | 0.59375
| 7 | 0.58958 | 0.58958 | 0.59028 | 0.59028 | 0.59028 | 0.59028 | 0.59028 | 0.59028 | 0.59028 | 0.59028 | 0.59097 | 0.59097 | 0.59097 | 0.59097 | 0.59097 | 0.59097 | 0.59097
| 7.5 | 0.54236 | 0.54236 | 0.54306 | 0.54375 | 0.54444 | 0.54583 | 0.54653 | 0.54722 | 0.54792 | 0.54861 | 0.55 | 0.55 | 0.55069 | 0.55139 | 0.55208 | 0.55278 | 0.55417
| 8 | 0.49861 | 0.49861 | 0.5 | 0.50139 | 0.50278 | 0.50417 | 0.50556 | 0.50694 | 0.50764 | 0.50903 | 0.51111 | 0.51181 | 0.51319 | 0.51389 | 0.51597 | 0.51667 | 0.51875
| 8.5 | 0.45972 | 0.45972 | 0.46111 | 0.4625 | 0.46458 | 0.46667 | 0.46875 | 0.47014 | 0.47153 | 0.47292 | 0.47569 | 0.47639 | 0.47847 | 0.47917 | 0.48194 | 0.48264 | 0.48542
| 9 | 0.42431 | 0.425 | 0.42639 | 0.42778 | 0.42986 | 0.43194 | 0.43472 | 0.43611 | 0.4375 | 0.43958 | 0.44236 | 0.44306 | 0.44583 | 0.44653 | 0.44931 | 0.45 | 0.45347
| 9.5 | 0.39236 | 0.39306 | 0.39514 | 0.39653 | 0.39861 | 0.40139 | 0.40347 | 0.40556 | 0.40694 | 0.40833 | 0.41181 | 0.4125 | 0.41528 | 0.41597 | 0.41875 | 0.40694 | 0.39444
| 10 | 0.36389 | 0.36458 | 0.36667 | 0.36806 | 0.37083 | 0.37292 | 0.375 | 0.37708 | 0.37847 | 0.38056 | 0.37917 | 0.36597 | 0.35486 | 0.34444 | 0.33542 | 0.32708 | 0.31875
| 10.5 | 0.33819 | 0.33889 | 0.34028 | 0.34236 | 0.34444 | 0.34653 | 0.34931 | 0.33958 | 0.32847 | 0.31875 | 0.30972 | 0.30139 | 0.29375 | 0.28611 | 0.27917 | 0.27292 | 0.26667
| 11 | 0.31458 | 0.31528 | 0.31667 | 0.31875 | 0.31181 | 0.30139 | 0.29167 | 0.28333 | 0.27569 | 0.26806 | 0.26111 | 0.25486 | 0.24861 | 0.24306 | 0.2375 | 0.23264 | 0.22778
| 11.5 | 0.29306 | 0.29236 | 0.28125 | 0.27222 | 0.26389 | 0.25625 | 0.24861 | 0.24236 | 0.23611 | 0.22986 | 0.22431 | 0.21944 | 0.21458 | 0.20972 | 0.20486 | 0.20069 | 0.19653
| 12 | 0.25764 | 0.24931 | 0.24167 | 0.23403 | 0.22778 | 0.22153 | 0.21528 | 0.20972 | 0.20486 | 0.2 | 0.19514 | 0.19097 | 0.18681 | 0.18264 | 0.17917 | 0.175 | 0.17222
| 12.5 | 0.22361 | 0.21667 | 0.21042 | 0.20417 | 0.19861 | 0.19375 | 0.18889 | 0.18403 | 0.17986 | 0.17569 | 0.17153 | 0.16806 | 0.16389 | 0.16042 | 0.15764 | 0.15417 | 0.15139
| 13 | 0.19583 | 0.19028 | 0.18472 | 0.17986 | 0.175 | 0.17083 | 0.16667 | 0.1625 | 0.15903 | 0.15556 | 0.15139 | 0.14861 | 0.14514 | 0.14236 | 0.13958 | 0.13681 | 0.13403
| 13.5 | 0.17361 | 0.16875 | 0.16389 | 0.15972 | 0.15556 | 0.15139 | 0.14792 | 0.14444 | 0.14167 | 0.13819 | 0.13542 | 0.13264 | 0.12986 | 0.12708 | 0.12431 | 0.12222 | 0.12014
| 14 | 0.15486 | 0.15069 | 0.14653 | 0.14306 | 0.13889 | 0.13542 | 0.13264 | 0.12917 | 0.12639 | 0.12361 | 0.12083 | 0.11875 | 0.11597 | 0.11389 | 0.11181 | 0.10972 | 0.10764
| 14.5 | 0.13889 | 0.13542 | 0.13194 | 0.12847 | 0.125 | 0.12222 | 0.11944 | 0.11667 | 0.11389 | 0.11111 | 0.10903 | 0.10694 | 0.10486 | 0.10278 | 0.10069 | 0.098611 | 0.097222
| 15 | 0.125 | 0.12222 | 0.11875 | 0.11597 | 0.11319 | 0.11042 | 0.10764 | 0.10556 | 0.10278 | 0.10069 | 0.098611 | 0.096528 | 0.095139 | 0.093056 | 0.091667 | 0.089583 | 0.088194
| 15.5 | 0.11389 | 0.11042 | 0.10764 | 0.10486 | 0.10278 | 0.1 | 0.097917 | 0.095833 | 0.09375 | 0.091667 | 0.089583 | 0.088194 | 0.086111 | 0.084722 | 0.083333 | 0.081944 | 0.080556
| 16 | 0.10347 | 0.10069 | 0.097917 | 0.095833 | 0.09375 | 0.091667 | 0.089583 | 0.0875 | 0.085417 | 0.084028 | 0.081944 | 0.080556 | 0.079167 | 0.077778 | 0.075694 | 0.075 | 0.073611
| 16.5 | 0.094444 | 0.091667 | 0.089583 | 0.0875 | 0.085417 | 0.083333 | 0.081944 | 0.079861 | 0.078472 | 0.076389 | 0.075 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.099 | 0.097
| 17 | 0.086806 | 0.084722 | 0.082639 | 0.080556 | 0.078472 | 0.076389 | 0.075 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092 | 0.091 | 0.089
| 17.5 | 0.079861 | 0.077778 | 0.075694 | 0.074306 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.087 | 0.085 | 0.084 | 0.082
| 18 | 0.073611 | 0.071528 | 0.070139 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.087 | 0.085 | 0.083 | 0.082 | 0.08 | 0.079 | 0.078 | 0.076
| 18.5 | 0.098 | 0.096 | 0.093 | 0.091 | 0.089 | 0.087 | 0.085 | 0.084 | 0.082 | 0.08 | 0.079 | 0.077 | 0.076 | 0.075 | 0.073 | 0.072 | 0.071
| 19 | 0.091 | 0.089 | 0.087 | 0.085 | 0.083 | 0.081 | 0.079 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.071 | 0.069 | 0.068 | 0.067 | 0.066
| 19.5 | 0.085 | 0.083 | 0.081 | 0.079 | 0.077 | 0.076 | 0.074 | 0.072 | 0.071 | 0.07 | 0.068 | 0.067 | 0.066 | 0.065 | 0.064 | 0.063 | 0.062
| 20 | 0.079 | 0.077 | 0.075 | 0.074 | 0.072 | 0.07 | 0.069 | 0.068 | 0.066 | 0.065 | 0.064 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058
| 20.5 | 0.073 | 0.071 | 0.069 | 0.068 | 0.067 | 0.065 | 0.064 | 0.063 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056 | 0.056 | 0.055 | 0.054
| 21 | 0.067 | 0.065 | 0.063 | 0.062 | 0.061 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.051 | 0.05 | 0.049
| 21.5 | 0.059 | 0.058 | 0.056 | 0.056 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.047 | 0.046 | 0.045 | 0.044 | 0.044
| 22 | 0.052 | 0.051 | 0.049 | 0.049 | 0.047 | 0.046 | 0.045 | 0.045 | 0.043 | 0.043 | 0.042 | 0.041 | 0.041 | 0.04 | 0.039 | 0.039 | 0.038
| 22.5 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032
| 23 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.032 | 0.031 | 0.031 | 0.03 | 0.03
| 23.5 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.031 | 0.031 | 0.03 | 0.03 | 0.029 | 0.029 | 0.028 | 0.028
| 24 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032 | 0.031 | 0.031 | 0.03 | 0.029 | 0.029 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026
| 24.5 | 0.033 | 0.033 | 0.032 | 0.031 | 0.031 | 0.03 | 0.029 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.026 | 0.025 | 0.025 | 0.025
| 25 | 0.031 | 0.03 | 0.03 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.024 | 0.023 | 0.023