## Sheet1
PROPERTIES
General
Name | Nordex N131/3.9 Mode 9 2,86MW
Manufacturer | Nordex
Hub Height | 84 | 114 | 120 | 134 | 164
Power
Rated Power | 2860
Peak Power | 2860
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 131
Number of blades | 3
Rated RPM | 12.6
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 25
Restart Wind Speed | 19.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 40
High Temperature Restart | 38
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | III
Turbine SubClass | S
Values
Certification | IEC 3rd Edition
Vave | 7.5
Vref | 40
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 1 | 3 | 4 | 5 | 7 | 8 | 9 | 10 | 12 | 13 | 14 | 15 | 17 | 18 | 19 | 21 | 22
| 3.5 | 52 | 55 | 58 | 60 | 63 | 66 | 69 | 71 | 74 | 77 | 79 | 82 | 85 | 87 | 90 | 93 | 95
| 4 | 122 | 127 | 132 | 136 | 141 | 145 | 150 | 155 | 159 | 164 | 169 | 173 | 178 | 182 | 187 | 192 | 196
| 4.5 | 210 | 217 | 224 | 232 | 239 | 246 | 253 | 260 | 267 | 274 | 281 | 288 | 295 | 302 | 309 | 316 | 323
| 5 | 317 | 327 | 337 | 347 | 357 | 367 | 377 | 387 | 397 | 407 | 417 | 427 | 437 | 446 | 456 | 466 | 476
| 5.5 | 442 | 456 | 469 | 482 | 496 | 509 | 523 | 536 | 550 | 563 | 576 | 590 | 603 | 617 | 630 | 643 | 657
| 6 | 589 | 606 | 624 | 641 | 659 | 676 | 693 | 711 | 728 | 746 | 763 | 781 | 798 | 815 | 833 | 850 | 867
| 6.5 | 761 | 783 | 805 | 827 | 849 | 871 | 893 | 915 | 938 | 960 | 982 | 1004 | 1026 | 1048 | 1069 | 1091 | 1113
| 7 | 953 | 981 | 1008 | 1036 | 1064 | 1091 | 1118 | 1146 | 1173 | 1201 | 1228 | 1256 | 1283 | 1311 | 1338 | 1366 | 1393
| 7.5 | 1157 | 1190 | 1224 | 1258 | 1291 | 1324 | 1358 | 1392 | 1425 | 1458 | 1492 | 1526 | 1561 | 1595 | 1629 | 1662 | 1695
| 8 | 1363 | 1402 | 1443 | 1483 | 1523 | 1563 | 1603 | 1643 | 1683 | 1723 | 1763 | 1805 | 1847 | 1889 | 1929 | 1970 | 2011
| 8.5 | 1567 | 1613 | 1661 | 1707 | 1755 | 1800 | 1848 | 1895 | 1941 | 1987 | 2034 | 2085 | 2136 | 2188 | 2235 | 2280 | 2319
| 9 | 1768 | 1821 | 1876 | 1930 | 1984 | 2036 | 2091 | 2143 | 2197 | 2252 | 2307 | 2357 | 2405 | 2454 | 2498 | 2534 | 2563
| 9.5 | 1969 | 2027 | 2090 | 2150 | 2211 | 2269 | 2332 | 2388 | 2436 | 2484 | 2533 | 2573 | 2609 | 2646 | 2678 | 2704 | 2724
| 10 | 2166 | 2231 | 2300 | 2367 | 2431 | 2480 | 2535 | 2582 | 2618 | 2655 | 2692 | 2720 | 2746 | 2771 | 2794 | 2809 | 2819
| 10.5 | 2360 | 2430 | 2493 | 2550 | 2602 | 2640 | 2683 | 2718 | 2743 | 2769 | 2795 | 2812 | 2825 | 2839 | 2851 | 2856 | 2857
| 11 | 2532 | 2591 | 2640 | 2684 | 2725 | 2752 | 2782 | 2805 | 2820 | 2835 | 2850 | 2855 | 2857 | 2859 | 2860 | 2860 | 2860
| 11.5 | 2663 | 2708 | 2745 | 2777 | 2805 | 2821 | 2839 | 2852 | 2855 | 2858 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860
| 12 | 2756 | 2789 | 2814 | 2833 | 2849 | 2854 | 2859 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860
| 12.5 | 2817 | 2838 | 2850 | 2857 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860
| 13 | 2850 | 2858 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860
| 13.5 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860
| 14 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860
| 14.5 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860
| 15 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860
| 15.5 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860
| 16 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860
| 16.5 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860
| 17 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860
| 17.5 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860
| 18 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860
| 18.5 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860
| 19 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860
| 19.5 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860
| 20 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860
| 20.5 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860
| 21 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860
| 21.5 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860
| 22 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860
| 22.5 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860
| 23 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860 | 2860
| 23.5 | 2859 | 2859 | 2859 | 2859 | 2859 | 2859 | 2859 | 2859 | 2859 | 2859 | 2859 | 2859 | 2859 | 2859 | 2859 | 2859 | 2859
| 24 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852
| 24.5 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835 | 2835
| 25 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820 | 2820

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.62639 | 0.62639 | 0.62639 | 0.62639 | 0.62708 | 0.62778 | 0.62847 | 0.62917 | 0.62986 | 0.63056 | 0.63056 | 0.63194 | 0.63264 | 0.63264 | 0.63333 | 0.63403 | 0.63472
| 3.5 | 0.62153 | 0.62222 | 0.62292 | 0.62361 | 0.62361 | 0.62431 | 0.625 | 0.62569 | 0.62569 | 0.62639 | 0.62639 | 0.62708 | 0.62708 | 0.62778 | 0.62778 | 0.62847 | 0.62847
| 4 | 0.61736 | 0.61736 | 0.61806 | 0.61806 | 0.61875 | 0.61875 | 0.61875 | 0.61944 | 0.61944 | 0.61944 | 0.62014 | 0.62014 | 0.62014 | 0.62083 | 0.62083 | 0.62083 | 0.62083
| 4.5 | 0.6125 | 0.6125 | 0.6125 | 0.6125 | 0.61319 | 0.61319 | 0.61319 | 0.61319 | 0.61319 | 0.61319 | 0.61319 | 0.61389 | 0.61389 | 0.61389 | 0.61389 | 0.61389 | 0.61389
| 5 | 0.60833 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60694 | 0.60694 | 0.60694 | 0.60764 | 0.60694 | 0.60764
| 5.5 | 0.60208 | 0.60208 | 0.60208 | 0.60139 | 0.60139 | 0.60139 | 0.60139 | 0.60069 | 0.60069 | 0.60069 | 0.60069 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
| 6 | 0.59861 | 0.59861 | 0.59792 | 0.59792 | 0.59792 | 0.59722 | 0.59722 | 0.59722 | 0.59722 | 0.59653 | 0.59653 | 0.59653 | 0.59583 | 0.59583 | 0.59583 | 0.59583 | 0.59583
| 6.5 | 0.59653 | 0.59653 | 0.59583 | 0.59583 | 0.59583 | 0.59583 | 0.59583 | 0.59514 | 0.59514 | 0.59514 | 0.59514 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59444
| 7 | 0.57292 | 0.57361 | 0.57361 | 0.57431 | 0.57431 | 0.57431 | 0.575 | 0.575 | 0.57569 | 0.57569 | 0.57569 | 0.57639 | 0.57708 | 0.57778 | 0.57778 | 0.57778 | 0.57847
| 7.5 | 0.525 | 0.525 | 0.52639 | 0.52708 | 0.52778 | 0.52847 | 0.52986 | 0.53056 | 0.53056 | 0.53194 | 0.53264 | 0.53403 | 0.53542 | 0.5375 | 0.5375 | 0.53889 | 0.53958
| 8 | 0.48056 | 0.48194 | 0.48333 | 0.48472 | 0.48611 | 0.48681 | 0.48819 | 0.48889 | 0.49028 | 0.49097 | 0.49236 | 0.49444 | 0.49722 | 0.5 | 0.50069 | 0.50208 | 0.50347
| 8.5 | 0.44167 | 0.44306 | 0.44514 | 0.44653 | 0.44792 | 0.44861 | 0.45069 | 0.45139 | 0.45278 | 0.45417 | 0.45556 | 0.45833 | 0.46111 | 0.46458 | 0.46528 | 0.46806 | 0.46875
| 9 | 0.40694 | 0.40833 | 0.41042 | 0.41181 | 0.41389 | 0.41458 | 0.41667 | 0.41806 | 0.41944 | 0.42083 | 0.42222 | 0.425 | 0.42847 | 0.43194 | 0.43264 | 0.43542 | 0.43681
| 9.5 | 0.37569 | 0.37708 | 0.37917 | 0.38125 | 0.38333 | 0.38403 | 0.38611 | 0.3875 | 0.38889 | 0.39028 | 0.39167 | 0.39514 | 0.39792 | 0.40208 | 0.40347 | 0.39514 | 0.38264
| 10 | 0.34792 | 0.34931 | 0.35139 | 0.35347 | 0.35486 | 0.35625 | 0.35833 | 0.35972 | 0.36111 | 0.3625 | 0.36528 | 0.35625 | 0.34514 | 0.33542 | 0.32639 | 0.31806 | 0.31042
| 10.5 | 0.32292 | 0.32431 | 0.32639 | 0.32778 | 0.32986 | 0.33056 | 0.33403 | 0.33125 | 0.32014 | 0.31042 | 0.30139 | 0.29375 | 0.28611 | 0.27917 | 0.27222 | 0.26597 | 0.26042
| 11 | 0.3 | 0.30139 | 0.30347 | 0.30625 | 0.30486 | 0.29375 | 0.28472 | 0.27639 | 0.26875 | 0.26181 | 0.25486 | 0.24861 | 0.24306 | 0.2375 | 0.23194 | 0.22708 | 0.22222
| 11.5 | 0.27986 | 0.28264 | 0.275 | 0.26528 | 0.25764 | 0.25 | 0.24306 | 0.23611 | 0.23056 | 0.225 | 0.21944 | 0.21389 | 0.20903 | 0.20486 | 0.2 | 0.19583 | 0.19236
| 12 | 0.25208 | 0.24306 | 0.23542 | 0.22847 | 0.22222 | 0.21597 | 0.21042 | 0.20486 | 0.2 | 0.19514 | 0.19097 | 0.18681 | 0.18264 | 0.17847 | 0.175 | 0.17153 | 0.16806
| 12.5 | 0.21806 | 0.21181 | 0.20556 | 0.19931 | 0.19444 | 0.18889 | 0.18403 | 0.17986 | 0.17569 | 0.17153 | 0.16736 | 0.16389 | 0.16042 | 0.15694 | 0.15417 | 0.15069 | 0.14792
| 13 | 0.19167 | 0.18611 | 0.18056 | 0.17569 | 0.17083 | 0.16667 | 0.1625 | 0.15903 | 0.15556 | 0.15139 | 0.14861 | 0.14514 | 0.14236 | 0.13889 | 0.13611 | 0.13403 | 0.13125
| 13.5 | 0.16944 | 0.16458 | 0.16042 | 0.15625 | 0.15208 | 0.14861 | 0.14444 | 0.14167 | 0.13819 | 0.13472 | 0.13194 | 0.12917 | 0.12639 | 0.12431 | 0.12153 | 0.11944 | 0.11736
| 14 | 0.15139 | 0.14722 | 0.14306 | 0.13958 | 0.13611 | 0.13264 | 0.12986 | 0.12639 | 0.12361 | 0.12083 | 0.11875 | 0.11597 | 0.11389 | 0.11111 | 0.10903 | 0.10694 | 0.10556
| 14.5 | 0.13611 | 0.13194 | 0.12847 | 0.12569 | 0.12222 | 0.11944 | 0.11667 | 0.11389 | 0.11111 | 0.10903 | 0.10694 | 0.10486 | 0.10278 | 0.10069 | 0.098611 | 0.096528 | 0.095139
| 15 | 0.12222 | 0.11944 | 0.11597 | 0.11319 | 0.11042 | 0.10764 | 0.10556 | 0.10278 | 0.10069 | 0.098611 | 0.096528 | 0.094444 | 0.093056 | 0.090972 | 0.089583 | 0.0875 | 0.086111
| 15.5 | 0.11111 | 0.10833 | 0.10556 | 0.10278 | 0.1 | 0.097917 | 0.095833 | 0.09375 | 0.091667 | 0.089583 | 0.088194 | 0.086111 | 0.084722 | 0.082639 | 0.08125 | 0.079861 | 0.078472
| 16 | 0.10139 | 0.098611 | 0.095833 | 0.09375 | 0.091667 | 0.089583 | 0.0875 | 0.085417 | 0.083333 | 0.081944 | 0.080556 | 0.078472 | 0.077083 | 0.075694 | 0.074306 | 0.072917 | 0.071528
| 16.5 | 0.092361 | 0.090278 | 0.0875 | 0.085417 | 0.083333 | 0.081944 | 0.079861 | 0.078472 | 0.076389 | 0.075 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.095
| 17 | 0.084722 | 0.082639 | 0.080556 | 0.078472 | 0.077083 | 0.075 | 0.073611 | 0.072222 | 0.070139 | 0.099 | 0.097 | 0.096 | 0.094 | 0.092 | 0.09 | 0.089 | 0.087
| 17.5 | 0.077778 | 0.076389 | 0.074306 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.086 | 0.085 | 0.084 | 0.082 | 0.081
| 18 | 0.072222 | 0.070139 | 0.099 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083 | 0.082 | 0.08 | 0.079 | 0.077 | 0.076 | 0.075
| 18.5 | 0.096 | 0.094 | 0.091 | 0.089 | 0.087 | 0.085 | 0.084 | 0.082 | 0.08 | 0.079 | 0.077 | 0.076 | 0.074 | 0.073 | 0.072 | 0.071 | 0.069
| 19 | 0.089 | 0.087 | 0.085 | 0.083 | 0.081 | 0.079 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.07 | 0.069 | 0.068 | 0.067 | 0.066 | 0.065
| 19.5 | 0.083 | 0.081 | 0.079 | 0.077 | 0.076 | 0.074 | 0.072 | 0.071 | 0.07 | 0.068 | 0.067 | 0.066 | 0.064 | 0.063 | 0.062 | 0.061 | 0.06
| 20 | 0.077 | 0.076 | 0.074 | 0.072 | 0.07 | 0.069 | 0.068 | 0.066 | 0.065 | 0.064 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056
| 20.5 | 0.071 | 0.07 | 0.068 | 0.067 | 0.065 | 0.064 | 0.063 | 0.061 | 0.06 | 0.059 | 0.057 | 0.056 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052
| 21 | 0.065 | 0.064 | 0.062 | 0.061 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.052 | 0.051 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047
| 21.5 | 0.058 | 0.057 | 0.056 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.044 | 0.043 | 0.042
| 22 | 0.051 | 0.05 | 0.049 | 0.047 | 0.046 | 0.045 | 0.045 | 0.043 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.038 | 0.037 | 0.037
| 22.5 | 0.043 | 0.043 | 0.041 | 0.04 | 0.039 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032 | 0.032 | 0.031
| 23 | 0.039 | 0.039 | 0.038 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.031 | 0.031 | 0.03 | 0.03 | 0.029 | 0.029
| 23.5 | 0.037 | 0.037 | 0.036 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.031 | 0.031 | 0.03 | 0.029 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027
| 24 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032 | 0.031 | 0.031 | 0.03 | 0.029 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.026 | 0.025
| 24.5 | 0.033 | 0.032 | 0.031 | 0.031 | 0.03 | 0.029 | 0.029 | 0.028 | 0.028 | 0.027 | 0.026 | 0.026 | 0.025 | 0.025 | 0.025 | 0.024 | 0.024
| 25 | 0.03 | 0.03 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.026 | 0.025 | 0.024 | 0.024 | 0.024 | 0.023 | 0.023 | 0.023 | 0.022