## Sheet1
PROPERTIES
General
Name | Nordex N133/4.X Mode 1 125m 4,7MW
Manufacturer | Nordex
Hub Height | 125
Power
Rated Power | 4700
Peak Power | 4700
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 133
Number of blades | 3
Rated RPM | 11.4
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 28
Restart Wind Speed | 22
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 40
High Temperature Restart | 38
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | S
Values
Certification | IEC 3rd Edition
Vave | 9
Vref | 47
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 20 | 22 | 24 | 26 | 27 | 29 | 31 | 33 | 34 | 36 | 38 | 40 | 42
| 3.5 | 76 | 80 | 83 | 86 | 89 | 92 | 95 | 99 | 102 | 105 | 108 | 111 | 115
| 4 | 154 | 159 | 164 | 169 | 175 | 180 | 185 | 190 | 195 | 200 | 205 | 210 | 216
| 4.5 | 251 | 258 | 266 | 273 | 281 | 289 | 296 | 304 | 311 | 319 | 326 | 334 | 341
| 5 | 367 | 378 | 388 | 399 | 409 | 420 | 430 | 441 | 451 | 461 | 472 | 482 | 493
| 5.5 | 507 | 521 | 535 | 549 | 563 | 577 | 591 | 604 | 618 | 632 | 646 | 660 | 674
| 6 | 673 | 691 | 709 | 727 | 745 | 763 | 781 | 799 | 817 | 835 | 853 | 871 | 889
| 6.5 | 869 | 891 | 914 | 937 | 960 | 983 | 1006 | 1028 | 1051 | 1074 | 1097 | 1120 | 1142
| 7 | 1096 | 1124 | 1153 | 1181 | 1210 | 1238 | 1267 | 1295 | 1323 | 1352 | 1380 | 1408 | 1437
| 7.5 | 1357 | 1392 | 1427 | 1462 | 1497 | 1532 | 1567 | 1601 | 1636 | 1671 | 1705 | 1740 | 1775
| 8 | 1655 | 1697 | 1739 | 1781 | 1823 | 1865 | 1907 | 1949 | 1991 | 2033 | 2075 | 2117 | 2159
| 8.5 | 1986 | 2036 | 2086 | 2137 | 2187 | 2237 | 2287 | 2337 | 2386 | 2434 | 2481 | 2527 | 2572
| 9 | 2336 | 2394 | 2453 | 2512 | 2570 | 2629 | 2687 | 2746 | 2799 | 2850 | 2898 | 2944 | 2988
| 9.5 | 2685 | 2752 | 2819 | 2886 | 2953 | 3020 | 3086 | 3154 | 3209 | 3259 | 3306 | 3351 | 3393
| 10 | 3021 | 3096 | 3172 | 3247 | 3321 | 3396 | 3472 | 3549 | 3605 | 3654 | 3697 | 3736 | 3773
| 10.5 | 3338 | 3421 | 3503 | 3586 | 3669 | 3753 | 3830 | 3910 | 3961 | 4003 | 4036 | 4065 | 4092
| 11 | 3630 | 3720 | 3811 | 3898 | 3979 | 4060 | 4125 | 4191 | 4231 | 4262 | 4286 | 4306 | 4325
| 11.5 | 3902 | 3992 | 4077 | 4156 | 4222 | 4289 | 4342 | 4396 | 4426 | 4449 | 4465 | 4479 | 4492
| 12 | 4135 | 4214 | 4284 | 4349 | 4403 | 4457 | 4497 | 4539 | 4560 | 4577 | 4587 | 4596 | 4604
| 12.5 | 4318 | 4383 | 4440 | 4492 | 4533 | 4574 | 4603 | 4632 | 4646 | 4657 | 4661 | 4666 | 4670
| 13 | 4458 | 4510 | 4554 | 4592 | 4621 | 4650 | 4667 | 4683 | 4691 | 4696 | 4696 | 4697 | 4697
| 13.5 | 4561 | 4600 | 4631 | 4657 | 4674 | 4691 | 4696 | 4699 | 4700 | 4700 | 4700 | 4700 | 4700
| 14 | 4632 | 4659 | 4678 | 4692 | 4696 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 14.5 | 4677 | 4691 | 4697 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 15 | 4697 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 15.5 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 16 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 16.5 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 17 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 17.5 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 18 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 18.5 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 19 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 19.5 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 20 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 20.5 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 21 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 21.5 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 22 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 22.5 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 23 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 23.5 | 4694 | 4694 | 4694 | 4694 | 4694 | 4694 | 4694 | 4694 | 4694 | 4694 | 4694 | 4694 | 4694
| 24 | 4673 | 4673 | 4673 | 4673 | 4673 | 4673 | 4673 | 4673 | 4673 | 4673 | 4673 | 4673 | 4673
| 24.5 | 4637 | 4637 | 4637 | 4637 | 4637 | 4637 | 4637 | 4637 | 4637 | 4637 | 4637 | 4637 | 4637
| 25 | 4594 | 4594 | 4594 | 4594 | 4594 | 4594 | 4594 | 4594 | 4594 | 4594 | 4594 | 4594 | 4594
| 25.5 | 4550 | 4550 | 4550 | 4550 | 4550 | 4550 | 4550 | 4550 | 4550 | 4550 | 4550 | 4550 | 4550
| 26 | 4502 | 4502 | 4502 | 4502 | 4502 | 4502 | 4502 | 4502 | 4502 | 4502 | 4502 | 4502 | 4502
| 26.5 | 4459 | 4459 | 4459 | 4459 | 4459 | 4459 | 4459 | 4459 | 4459 | 4459 | 4459 | 4459 | 4459
| 27 | 4411 | 4411 | 4411 | 4411 | 4411 | 4411 | 4411 | 4411 | 4411 | 4411 | 4411 | 4411 | 4411
| 27.5 | 4368 | 4368 | 4368 | 4368 | 4368 | 4368 | 4368 | 4368 | 4368 | 4368 | 4368 | 4368 | 4368
| 28 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931
| 3.5 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236
| 4 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264
| 4.5 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569
| 5 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014
| 5.5 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667
| 6 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389
| 6.5 | 0.56319 | 0.56319 | 0.56319 | 0.56319 | 0.56319 | 0.56319 | 0.56319 | 0.56319 | 0.56319 | 0.56319 | 0.56319 | 0.56319 | 0.56319
| 7 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.56319 | 0.56319 | 0.56319 | 0.56319 | 0.5625
| 7.5 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56111 | 0.56111 | 0.56042 | 0.55972 | 0.55764
| 8 | 0.55486 | 0.55486 | 0.55486 | 0.55486 | 0.55486 | 0.55486 | 0.55486 | 0.55486 | 0.55278 | 0.55069 | 0.54861 | 0.54583 | 0.54306
| 8.5 | 0.53958 | 0.53958 | 0.53958 | 0.53958 | 0.53958 | 0.53958 | 0.53958 | 0.53958 | 0.53611 | 0.53333 | 0.52986 | 0.52639 | 0.52222
| 9 | 0.51944 | 0.51944 | 0.51944 | 0.51944 | 0.51944 | 0.51944 | 0.51944 | 0.51944 | 0.51528 | 0.51111 | 0.50694 | 0.50278 | 0.49792
| 9.5 | 0.49514 | 0.49514 | 0.49514 | 0.49514 | 0.49514 | 0.49583 | 0.49514 | 0.49514 | 0.49028 | 0.48472 | 0.47986 | 0.47431 | 0.46875
| 10 | 0.46944 | 0.46944 | 0.46944 | 0.46944 | 0.46875 | 0.46806 | 0.46597 | 0.46528 | 0.45903 | 0.45347 | 0.44792 | 0.44236 | 0.43611
| 10.5 | 0.44236 | 0.44167 | 0.44097 | 0.43958 | 0.43819 | 0.43681 | 0.43403 | 0.43264 | 0.42639 | 0.42083 | 0.41458 | 0.40833 | 0.40208
| 11 | 0.41319 | 0.41181 | 0.41042 | 0.40833 | 0.40625 | 0.40417 | 0.40139 | 0.39931 | 0.39306 | 0.38611 | 0.38056 | 0.37431 | 0.36736
| 11.5 | 0.38264 | 0.38056 | 0.37847 | 0.37639 | 0.37361 | 0.37083 | 0.36806 | 0.36528 | 0.35903 | 0.35278 | 0.34653 | 0.34028 | 0.33333
| 12 | 0.35139 | 0.34931 | 0.34653 | 0.34444 | 0.34097 | 0.33889 | 0.33542 | 0.33264 | 0.32569 | 0.31944 | 0.31319 | 0.30694 | 0.30069
| 12.5 | 0.32083 | 0.31875 | 0.31597 | 0.31319 | 0.30972 | 0.30694 | 0.30347 | 0.3 | 0.29375 | 0.2875 | 0.28125 | 0.275 | 0.26944
| 13 | 0.29167 | 0.28889 | 0.28611 | 0.28333 | 0.27986 | 0.27708 | 0.27292 | 0.27014 | 0.26389 | 0.25833 | 0.25278 | 0.24722 | 0.24167
| 13.5 | 0.26528 | 0.2625 | 0.25903 | 0.25625 | 0.25278 | 0.24931 | 0.24583 | 0.24236 | 0.2375 | 0.23194 | 0.22708 | 0.22222 | 0.21736
| 14 | 0.24167 | 0.23819 | 0.23542 | 0.23194 | 0.22847 | 0.225 | 0.22153 | 0.21806 | 0.21319 | 0.20833 | 0.20417 | 0.19931 | 0.19514
| 14.5 | 0.22014 | 0.21667 | 0.21319 | 0.20972 | 0.20625 | 0.20347 | 0.19931 | 0.19583 | 0.19167 | 0.1875 | 0.18333 | 0.17917 | 0.17569
| 15 | 0.20069 | 0.19722 | 0.19375 | 0.19028 | 0.18681 | 0.18333 | 0.17986 | 0.17639 | 0.17222 | 0.16875 | 0.16458 | 0.16111 | 0.15764
| 15.5 | 0.18264 | 0.17986 | 0.17639 | 0.17292 | 0.16875 | 0.16597 | 0.16181 | 0.15833 | 0.15486 | 0.15139 | 0.14792 | 0.14514 | 0.14167
| 16 | 0.16667 | 0.16319 | 0.16042 | 0.15694 | 0.15278 | 0.14931 | 0.14583 | 0.14236 | 0.13958 | 0.13611 | 0.13333 | 0.13056 | 0.12847
| 16.5 | 0.15208 | 0.14861 | 0.14514 | 0.14236 | 0.13889 | 0.13542 | 0.13194 | 0.12917 | 0.12639 | 0.12361 | 0.12083 | 0.11875 | 0.11667
| 17 | 0.13889 | 0.13542 | 0.13194 | 0.12917 | 0.12569 | 0.12292 | 0.12014 | 0.11736 | 0.11528 | 0.1125 | 0.11042 | 0.10833 | 0.10625
| 17.5 | 0.12708 | 0.12361 | 0.12014 | 0.11736 | 0.11458 | 0.1125 | 0.10972 | 0.10764 | 0.10486 | 0.10278 | 0.10069 | 0.098611 | 0.097222
| 18 | 0.11597 | 0.11319 | 0.11042 | 0.10764 | 0.10556 | 0.10278 | 0.10069 | 0.098611 | 0.096528 | 0.094444 | 0.093056 | 0.090972 | 0.089583
| 18.5 | 0.10694 | 0.10417 | 0.10208 | 0.099306 | 0.097222 | 0.095139 | 0.093056 | 0.090972 | 0.089583 | 0.0875 | 0.085417 | 0.084028 | 0.082639
| 19 | 0.099306 | 0.096528 | 0.094444 | 0.092361 | 0.090278 | 0.088194 | 0.086111 | 0.084722 | 0.082639 | 0.08125 | 0.079861 | 0.078472 | 0.077083
| 19.5 | 0.092361 | 0.090278 | 0.088194 | 0.086111 | 0.084028 | 0.082639 | 0.080556 | 0.079167 | 0.077778 | 0.076389 | 0.074306 | 0.072917 | 0.071528
| 20 | 0.086806 | 0.084722 | 0.082639 | 0.08125 | 0.079167 | 0.077778 | 0.075694 | 0.074306 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.097
| 20.5 | 0.081944 | 0.079861 | 0.078472 | 0.076389 | 0.075 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.094 | 0.092
| 21 | 0.077778 | 0.075694 | 0.074306 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092 | 0.091 | 0.089 | 0.087
| 21.5 | 0.074306 | 0.072222 | 0.070833 | 0.069444 | 0.097 | 0.095 | 0.093 | 0.091 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083
| 22 | 0.070833 | 0.069444 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.088 | 0.086 | 0.084 | 0.083 | 0.081 | 0.08
| 22.5 | 0.096 | 0.094 | 0.091 | 0.089 | 0.087 | 0.085 | 0.083 | 0.082 | 0.081 | 0.079 | 0.078 | 0.076 | 0.075
| 23 | 0.089 | 0.088 | 0.085 | 0.083 | 0.082 | 0.08 | 0.078 | 0.077 | 0.075 | 0.074 | 0.073 | 0.071 | 0.07
| 23.5 | 0.084 | 0.082 | 0.079 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.07 | 0.069 | 0.068 | 0.066 | 0.066
| 24 | 0.078 | 0.077 | 0.074 | 0.073 | 0.071 | 0.07 | 0.068 | 0.067 | 0.066 | 0.064 | 0.064 | 0.062 | 0.061
| 24.5 | 0.073 | 0.072 | 0.07 | 0.068 | 0.067 | 0.065 | 0.064 | 0.063 | 0.062 | 0.06 | 0.06 | 0.058 | 0.058
| 25 | 0.069 | 0.068 | 0.065 | 0.064 | 0.063 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054
| 25.5 | 0.065 | 0.063 | 0.061 | 0.06 | 0.059 | 0.058 | 0.056 | 0.056 | 0.055 | 0.053 | 0.053 | 0.051 | 0.051
| 26 | 0.061 | 0.06 | 0.058 | 0.057 | 0.056 | 0.054 | 0.053 | 0.053 | 0.051 | 0.05 | 0.05 | 0.048 | 0.048
| 26.5 | 0.057 | 0.056 | 0.055 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.047 | 0.046 | 0.045
| 27 | 0.054 | 0.053 | 0.052 | 0.05 | 0.049 | 0.048 | 0.047 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042
| 27.5 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.042 | 0.041 | 0.04
| 28 | 0.049 | 0.048 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038